## System and Pumping Curves
| Pumps in Series curves |  |  | Discharge Piping Velocities
Pressure Head (ft) | 1 pump (on) | 2 Pumps on |  | 18 | gpm/sf
114 | 0 | 0 |  | 600 | sf
104 | 1000 | 2000 |  | 10800 | gpm
95 | 2000 | 4000
87.5 | 3000 | 6000 |  | Service | D (in) | V (ft/s)
80.5 | 4000 | 8000 |  | Pump Discharge | 20 | 11.0302
77 | 5000 | 10000 |  | Header | 24 | 7.6599
72 | 6000 | 12000
68.5 | 7000 | 14000
64 | 8000 | 16000
60 | 8600 | 17200
58 | 9000 | 18000
52 | 10000 | 20000
42 | 11000 | 22000
32 | 11800 | 23600
New Design Point Lines
0 | 11016
100 | 11016
Set Points Check
Backwash Rate | Pump Head (ft) Measured | Pump Head Actual, max | Pump head Actual, min
5000 | 64.68 | 64.68 | 64.68
6000 | 55.44 | 55.44 | 55.44
7000 | 50.82 | 50.82 | 50.82

## BWS System Curve-24in
SYSTEM CURVE
| Max Wet Well WSE | 5184.21 | HWL from current HGL
| Min. Wet Well EL | 5173.14 | Bottom EL + conversion + assumed 6 ft minimum
| Trough EL +3" | 5193.75
Underdrain Headloss |  | 36 | inches
Underdrain Headloss |  | 3
Fluidized Bed Headloss |  | 0.11 | ft
[29 empty] | Pump Curve with 18" 70% Open Control Valve | [25 empty] | Pump Curve with 18" 50% Open Control Valve | [25 empty] | Pump Curve with 18" 27.5% Open Control Valve | [25 empty] | Pump Curve with 18" 20% Open Control Valve
STATIC HEAD
Max. Total Static Head |  | 23.72 | [26 empty] | Flow |  | Suction Seg Area | Discharge Seg Area | Seg 1 Area | Seg 2 Area | Seg 3 Area | Suction Seg Vel | Discharge Seg Vel | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Suction Seg h_minor | Discharge Seg h_minor | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Suction Seg h_friction | Discharge h_friction | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | h_delta_max | h_delta_min | TDH Max | TDH Min | Flow |  | Suction Seg Area | Discharge Seg Area | Seg 1 Area | Seg 2 Area | Seg 3 Area | Suction Seg Vel | Discharge Seg Vel | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Suction Seg h_minor | Discharge Seg h_minor | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Suction Seg h_friction | Discharge h_friction | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | h_delta_max | h_delta_min | TDH Max | TDH Min | Flow |  | Suction Seg Area | Discharge Seg Area | Seg 1 Area | Seg 2 Area | Seg 3 Area | Suction Seg Vel | Discharge Seg Vel | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Suction Seg h_minor | Discharge Seg h_minor | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Suction Seg h_friction | Discharge h_friction | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | h_delta_max | h_delta_min | TDH Max | TDH Min | Flow |  | Suction Seg Area | Discharge Seg Area | Seg 1 Area | Seg 2 Area | Seg 3 Area | Suction Seg Vel | Discharge Seg Vel | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Suction Seg h_minor | Discharge Seg h_minor | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Suction Seg h_friction | Discharge h_friction | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | h_delta_max | h_delta_min | TDH Max | TDH Min
Min Total Static Head |  | 12.65 | [26 empty] | gpm | cfs | sf | sf | sf | sf | sf | fps | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | gpm | cfs | sf | sf | sf | sf | sf | fps | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | gpm | cfs | sf | sf | sf | sf | sf | fps | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | gpm | cfs | sf | sf | sf | sf | sf | fps | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft
[29 empty] | 0 | 0 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.72 | 12.65 | 23.72 | 12.65 | 0 | 0 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.72 | 12.65 | 23.72 | 12.65 | 0 | 0 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.72 | 12.65 | 23.72 | 12.65 | 0 | 0 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.72 | 12.65 | 23.72 | 12.65
FRICTION LOSS | [28 empty] | 500 | 1.115 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0.51108 | 0.51108 | 0.35492 | 0.35492 | 0.63096 | 0.0016629 | 0.0090041 | 0.0035208 | 0.0050543 | 0.090571 | 0.0019029 | 0.002775 | 0.011485 | 0.004201 | 2.1192e-08 | 23.72 | 12.65 | 23.8502 | 12.7802 | 500 | 1.115 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0.51108 | 0.51108 | 0.35492 | 0.35492 | 0.63096 | 0.0016629 | 0.0090041 | 0.0035208 | 0.031337 | 0.090571 | 0.0019029 | 0.002775 | 0.011485 | 0.004201 | 2.1192e-08 | 23.72 | 12.65 | 23.8765 | 12.8065 | 500 | 1.115 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0.51108 | 0.51108 | 0.35492 | 0.35492 | 0.63096 | 0.0016629 | 0.0090041 | 0.0035208 | 0.16649 | 0.5262 | 0.0019029 | 0.002775 | 0.011485 | 0.004201 | 2.1192e-08 | 23.72 | 12.65 | 24.4472 | 13.3772 | 500 | 1.115 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 0.51108 | 0.51108 | 0.35492 | 0.35492 | 0.63096 | 0.0016629 | 0.0090041 | 0.0035208 | 0.16649 | 1.1692 | 0.0019029 | 0.002775 | 0.011485 | 0.004201 | 2.1192e-08 | 23.72 | 12.65 | 25.0902 | 14.0202
Hazen Williams Coefficients |  | C_water | C_wastewater | [25 empty] | 1000 | 2.23 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.0222 | 1.0222 | 0.70983 | 0.70983 | 1.2619 | 0.0066517 | 0.036017 | 0.014083 | 0.020217 | 0.36228 | 0.0068599 | 0.010004 | 0.041405 | 0.015144 | 7.6396e-08 | 23.72 | 12.65 | 24.2327 | 13.1627 | 1000 | 2.23 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.0222 | 1.0222 | 0.70983 | 0.70983 | 1.2619 | 0.0066517 | 0.036017 | 0.014083 | 0.12535 | 0.36228 | 0.0068599 | 0.010004 | 0.041405 | 0.015144 | 7.6396e-08 | 23.72 | 12.65 | 24.3378 | 13.2678 | 1000 | 2.23 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.0222 | 1.0222 | 0.70983 | 0.70983 | 1.2619 | 0.0066517 | 0.036017 | 0.014083 | 0.66598 | 2.1048 | 0.0068599 | 0.010004 | 0.041405 | 0.015144 | 7.6396e-08 | 23.72 | 12.65 | 26.621 | 15.551 | 1000 | 2.23 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.0222 | 1.0222 | 0.70983 | 0.70983 | 1.2619 | 0.0066517 | 0.036017 | 0.014083 | 0.66598 | 4.6768 | 0.0068599 | 0.010004 | 0.041405 | 0.015144 | 7.6396e-08 | 23.72 | 12.65 | 29.1929 | 18.1229
DI |  | 80-120 | 80-110 | [25 empty] | 1500 | 3.345 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.5332 | 1.5332 | 1.0647 | 1.0647 | 1.8929 | 0.014966 | 0.081037 | 0.031687 | 0.045488 | 0.81514 | 0.014524 | 0.021181 | 0.087664 | 0.032064 | 1.6175e-07 | 23.72 | 12.65 | 24.8638 | 13.7938 | 1500 | 3.345 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.5332 | 1.5332 | 1.0647 | 1.0647 | 1.8929 | 0.014966 | 0.081037 | 0.031687 | 0.28203 | 0.81514 | 0.014524 | 0.021181 | 0.087664 | 0.032064 | 1.6175e-07 | 23.72 | 12.65 | 25.1003 | 14.0303 | 1500 | 3.345 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.5332 | 1.5332 | 1.0647 | 1.0647 | 1.8929 | 0.014966 | 0.081037 | 0.031687 | 1.4984 | 4.7358 | 0.014524 | 0.021181 | 0.087664 | 0.032064 | 1.6175e-07 | 23.72 | 12.65 | 30.2374 | 19.1674 | 1500 | 3.345 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 1.5332 | 1.5332 | 1.0647 | 1.0647 | 1.8929 | 0.014966 | 0.081037 | 0.031687 | 1.4984 | 10.5228 | 0.014524 | 0.021181 | 0.087664 | 0.032064 | 1.6175e-07 | 23.72 | 12.65 | 36.0244 | 24.9544
Steel |  | 110-130 | 110-130 | [25 empty] | 2000 | 4.46 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.0443 | 2.0443 | 1.4197 | 1.4197 | 2.5238 | 0.026607 | 0.14407 | 0.056332 | 0.080868 | 1.4491 | 0.02473 | 0.036065 | 0.14926 | 0.054596 | 2.7541e-07 | 23.72 | 12.65 | 25.7417 | 14.6717 | 2000 | 4.46 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.0443 | 2.0443 | 1.4197 | 1.4197 | 2.5238 | 0.026607 | 0.14407 | 0.056332 | 0.50139 | 1.4491 | 0.02473 | 0.036065 | 0.14926 | 0.054596 | 2.7541e-07 | 23.72 | 12.65 | 26.1622 | 15.0922 | 2000 | 4.46 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.0443 | 2.0443 | 1.4197 | 1.4197 | 2.5238 | 0.026607 | 0.14407 | 0.056332 | 2.6639 | 8.4193 | 0.02473 | 0.036065 | 0.14926 | 0.054596 | 2.7541e-07 | 23.72 | 12.65 | 35.2948 | 24.2248 | 2000 | 4.46 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.0443 | 2.0443 | 1.4197 | 1.4197 | 2.5238 | 0.026607 | 0.14407 | 0.056332 | 2.6639 | 18.7072 | 0.02473 | 0.036065 | 0.14926 | 0.054596 | 2.7541e-07 | 23.72 | 12.65 | 45.5827 | 34.5127
PVC |  | 135-150 | 130-145 | [25 empty] | 2500 | 5.575 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.5554 | 2.5554 | 1.7746 | 1.7746 | 3.1548 | 0.041573 | 0.2251 | 0.088019 | 0.12636 | 2.2643 | 0.037369 | 0.054496 | 0.22555 | 0.082498 | 4.1616e-07 | 23.72 | 12.65 | 26.8652 | 15.7952 | 2500 | 5.575 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.5554 | 2.5554 | 1.7746 | 1.7746 | 3.1548 | 0.041573 | 0.2251 | 0.088019 | 0.78342 | 2.2643 | 0.037369 | 0.054496 | 0.22555 | 0.082498 | 4.1616e-07 | 23.72 | 12.65 | 27.5223 | 16.4523 | 2500 | 5.575 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.5554 | 2.5554 | 1.7746 | 1.7746 | 3.1548 | 0.041573 | 0.2251 | 0.088019 | 4.1624 | 13.1551 | 0.037369 | 0.054496 | 0.22555 | 0.082498 | 4.1616e-07 | 23.72 | 12.65 | 41.792 | 30.722 | 2500 | 5.575 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 2.5554 | 2.5554 | 1.7746 | 1.7746 | 3.1548 | 0.041573 | 0.2251 | 0.088019 | 4.1624 | 29.23 | 0.037369 | 0.054496 | 0.22555 | 0.082498 | 4.1616e-07 | 23.72 | 12.65 | 57.8669 | 46.7969
[29 empty] | 3000 | 6.69 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.0665 | 3.0665 | 2.1295 | 2.1295 | 3.7858 | 0.059865 | 0.32415 | 0.12675 | 0.18195 | 3.2606 | 0.052359 | 0.076357 | 0.31603 | 0.11559 | 5.831e-07 | 23.72 | 12.65 | 28.2336 | 17.1636 | 3000 | 6.69 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.0665 | 3.0665 | 2.1295 | 2.1295 | 3.7858 | 0.059865 | 0.32415 | 0.12675 | 1.1281 | 3.2606 | 0.052359 | 0.076357 | 0.31603 | 0.11559 | 5.831e-07 | 23.72 | 12.65 | 29.1798 | 18.1098 | 3000 | 6.69 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.0665 | 3.0665 | 2.1295 | 2.1295 | 3.7858 | 0.059865 | 0.32415 | 0.12675 | 5.9938 | 18.9433 | 0.052359 | 0.076357 | 0.31603 | 0.11559 | 5.831e-07 | 23.72 | 12.65 | 49.7282 | 38.6582 | 3000 | 6.69 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.0665 | 3.0665 | 2.1295 | 2.1295 | 3.7858 | 0.059865 | 0.32415 | 0.12675 | 5.9938 | 42.0911 | 0.052359 | 0.076357 | 0.31603 | 0.11559 | 5.831e-07 | 23.72 | 12.65 | 72.876 | 61.806
Pump Suction Segment |  |  |  | Pump Suction Segment |  |  |  | Segment 1 (Existing 24" BWS Pipe) |  |  |  | Segment 2 (New 24" BWS Pipe) |  |  |  | Segment 3 (New 18" BWS Pipe) |  |  |  | Segment 2 (New 18" BWS Pipe) |  |  | Segment 2 (New 18" BWS Pipe) |  |  | Segment 2 (New 18" BWS Pipe) |  |  | 3500 | 7.805 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.5775 | 3.5775 | 2.4844 | 2.4844 | 4.4167 | 0.081483 | 0.4412 | 0.17252 | 0.24766 | 4.438 | 0.069638 | 0.10156 | 0.42032 | 0.15374 | 7.7552e-07 | 23.72 | 12.65 | 29.8461 | 18.7761 | 3500 | 7.805 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.5775 | 3.5775 | 2.4844 | 2.4844 | 4.4167 | 0.081483 | 0.4412 | 0.17252 | 1.5355 | 4.438 | 0.069638 | 0.10156 | 0.42032 | 0.15374 | 7.7552e-07 | 23.72 | 12.65 | 31.134 | 20.064 | 3500 | 7.805 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.5775 | 3.5775 | 2.4844 | 2.4844 | 4.4167 | 0.081483 | 0.4412 | 0.17252 | 8.1582 | 25.784 | 0.069638 | 0.10156 | 0.42032 | 0.15374 | 7.7552e-07 | 23.72 | 12.65 | 59.1026 | 48.0326 | 3500 | 7.805 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 3.5775 | 3.5775 | 2.4844 | 2.4844 | 4.4167 | 0.081483 | 0.4412 | 0.17252 | 8.1582 | 57.2907 | 0.069638 | 0.10156 | 0.42032 | 0.15374 | 7.7552e-07 | 23.72 | 12.65 | 90.6094 | 79.5394
hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | 4000 | 8.92 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.0886 | 4.0886 | 2.8393 | 2.8393 | 5.0477 | 0.10643 | 0.57626 | 0.22533 | 0.32347 | 5.7966 | 0.089152 | 0.13001 | 0.5381 | 0.19682 | 9.9284e-07 | 23.72 | 12.65 | 31.7021 | 20.6321 | 4000 | 8.92 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.0886 | 4.0886 | 2.8393 | 2.8393 | 5.0477 | 0.10643 | 0.57626 | 0.22533 | 2.0056 | 5.7966 | 0.089152 | 0.13001 | 0.5381 | 0.19682 | 9.9284e-07 | 23.72 | 12.65 | 33.3842 | 22.3142 | 4000 | 8.92 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.0886 | 4.0886 | 2.8393 | 2.8393 | 5.0477 | 0.10643 | 0.57626 | 0.22533 | 10.6556 | 33.677 | 0.089152 | 0.13001 | 0.5381 | 0.19682 | 9.9284e-07 | 23.72 | 12.65 | 69.9147 | 58.8447 | 4000 | 8.92 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.0886 | 4.0886 | 2.8393 | 2.8393 | 5.0477 | 0.10643 | 0.57626 | 0.22533 | 10.6556 | 74.8287 | 0.089152 | 0.13001 | 0.5381 | 0.19682 | 9.9284e-07 | 23.72 | 12.65 | 111.0664 | 99.9964
L = Length of pipe (ft) |  | 24 | ft | L = Length of pipe (ft) |  | 35 | ft | L = Length of pipe (ft) |  | 350 | ft | L = Length of pipe (ft) | 200 | ft |  | L = Length of pipe (ft) | 20 | ft | Review Pipe Length | L = Length of pipe (ft) | 20 |  | L = Length of pipe (ft) | 20 |  | L = Length of pipe (ft) | 20 |  | 4500 | 10.035 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.5997 | 4.5997 | 3.1942 | 3.1942 | 5.6786 | 0.1347 | 0.72934 | 0.28518 | 0.4094 | 7.3363 | 0.11086 | 0.16167 | 0.66911 | 0.24474 | 1.2346e-06 | 23.72 | 12.65 | 33.8012 | 22.7312 | 4500 | 10.035 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.5997 | 4.5997 | 3.1942 | 3.1942 | 5.6786 | 0.1347 | 0.72934 | 0.28518 | 2.5383 | 7.3363 | 0.11086 | 0.16167 | 0.66911 | 0.24474 | 1.2346e-06 | 23.72 | 12.65 | 35.9301 | 24.8601 | 4500 | 10.035 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.5997 | 4.5997 | 3.1942 | 3.1942 | 5.6786 | 0.1347 | 0.72934 | 0.28518 | 13.486 | 42.6225 | 0.11086 | 0.16167 | 0.66911 | 0.24474 | 1.2346e-06 | 23.72 | 12.65 | 82.1641 | 71.0941 | 4500 | 10.035 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 4.5997 | 4.5997 | 3.1942 | 3.1942 | 5.6786 | 0.1347 | 0.72934 | 0.28518 | 13.486 | 94.7051 | 0.11086 | 0.16167 | 0.66911 | 0.24474 | 1.2346e-06 | 23.72 | 12.65 | 134.2467 | 123.1767
D = Inner Diameter of pipe (in) |  | 20 | in | D = Inner Diameter of pipe (in) |  | 20 | in | D = Inner Diameter of pipe (in) |  | 24 | in | D = Inner Diameter of pipe (in) | 24 | in |  | D = Inner Diameter of pipe (in) | 18 | in |  | D = Inner Diameter of pipe (in) | 18 |  | D = Inner Diameter of pipe (in) | 18 |  | D = Inner Diameter of pipe (in) | 18 |  | 5000 | 11.15 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.1108 | 5.1108 | 3.5492 | 3.5492 | 6.3096 | 0.16629 | 0.90041 | 0.35208 | 0.50543 | 9.0571 | 0.13471 | 0.19646 | 0.81311 | 0.2974 | 1.5003e-06 | 23.72 | 12.65 | 36.143 | 25.073 | 5000 | 11.15 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.1108 | 5.1108 | 3.5492 | 3.5492 | 6.3096 | 0.16629 | 0.90041 | 0.35208 | 3.1337 | 9.0571 | 0.13471 | 0.19646 | 0.81311 | 0.2974 | 1.5003e-06 | 23.72 | 12.65 | 38.7713 | 27.7013 | 5000 | 11.15 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.1108 | 5.1108 | 3.5492 | 3.5492 | 6.3096 | 0.16629 | 0.90041 | 0.35208 | 16.6494 | 52.6203 | 0.13471 | 0.19646 | 0.81311 | 0.2974 | 1.5003e-06 | 23.72 | 12.65 | 95.8502 | 84.7802 | 5000 | 11.15 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.1108 | 5.1108 | 3.5492 | 3.5492 | 6.3096 | 0.16629 | 0.90041 | 0.35208 | 16.6494 | 116.9198 | 0.13471 | 0.19646 | 0.81311 | 0.2974 | 1.5003e-06 | 23.72 | 12.65 | 160.1497 | 149.0797
C = HW coefficient (table above) |  | 110 |  | C = HW coefficient (table above) |  | 110 |  | C = HW coefficient (table above) |  | 110 |  | C = HW coefficient (table above) | 140 |  |  | C = HW coefficient (table above) | 140 |  |  | C = HW coefficient (table above) | 140 |  | C = HW coefficient (table above) | 140 |  | C = HW coefficient (table above) | 140 |  | 5400 | 12.042 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.5196 | 5.5196 | 3.8331 | 3.8331 | 6.8144 | 0.19396 | 1.0502 | 0.41066 | 0.58953 | 10.5642 | 0.15533 | 0.22652 | 0.93752 | 0.34291 | 1.7298e-06 | 23.72 | 12.65 | 38.1909 | 27.1209 | 5400 | 12.042 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.5196 | 5.5196 | 3.8331 | 3.8331 | 6.8144 | 0.19396 | 1.0502 | 0.41066 | 3.6551 | 10.5642 | 0.15533 | 0.22652 | 0.93752 | 0.34291 | 1.7298e-06 | 23.72 | 12.65 | 41.2565 | 30.1865 | 5400 | 12.042 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.5196 | 5.5196 | 3.8331 | 3.8331 | 6.8144 | 0.19396 | 1.0502 | 0.41066 | 19.4199 | 61.3764 | 0.15533 | 0.22652 | 0.93752 | 0.34291 | 1.7298e-06 | 23.72 | 12.65 | 107.8334 | 96.7634 | 5400 | 12.042 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 5.5196 | 5.5196 | 3.8331 | 3.8331 | 6.8144 | 0.19396 | 1.0502 | 0.41066 | 19.4199 | 136.3753 | 0.15533 | 0.22652 | 0.93752 | 0.34291 | 1.7298e-06 | 23.72 | 12.65 | 182.8323 | 171.7623
[29 empty] | 6000 | 13.38 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.1329 | 6.1329 | 4.259 | 4.259 | 7.5715 | 0.23946 | 1.2966 | 0.50699 | 0.72781 | 13.0423 | 0.18876 | 0.27527 | 1.1393 | 0.41671 | 2.1021e-06 | 23.72 | 12.65 | 41.5531 | 30.4831 | 6000 | 13.38 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.1329 | 6.1329 | 4.259 | 4.259 | 7.5715 | 0.23946 | 1.2966 | 0.50699 | 4.5125 | 13.0423 | 0.18876 | 0.27527 | 1.1393 | 0.41671 | 2.1021e-06 | 23.72 | 12.65 | 45.3378 | 34.2678 | 6000 | 13.38 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.1329 | 6.1329 | 4.259 | 4.259 | 7.5715 | 0.23946 | 1.2966 | 0.50699 | 23.9751 | 75.7733 | 0.18876 | 0.27527 | 1.1393 | 0.41671 | 2.1021e-06 | 23.72 | 12.65 | 127.5315 | 116.4615 | 6000 | 13.38 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.1329 | 6.1329 | 4.259 | 4.259 | 7.5715 | 0.23946 | 1.2966 | 0.50699 | 23.9751 | 168.3646 | 0.18876 | 0.27527 | 1.1393 | 0.41671 | 2.1021e-06 | 23.72 | 12.65 | 220.1228 | 209.0528
[12 empty] | 50% Open 20" Control Valve |  |  |  | 35% Open 20" Control Valve |  |  |  | 27.5% Open 18" Control Valve |  |  | 20% Open 18" Control Valve |  |  | 70% Open 18" Control Valve |  |  | 6500 | 14.495 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.644 | 6.644 | 4.6139 | 4.6139 | 8.2025 | 0.28103 | 1.5217 | 0.59501 | 0.85417 | 15.3065 | 0.21888 | 0.3192 | 1.3211 | 0.48322 | 2.4376e-06 | 23.72 | 12.65 | 44.6209 | 33.5509 | 6500 | 14.495 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.644 | 6.644 | 4.6139 | 4.6139 | 8.2025 | 0.28103 | 1.5217 | 0.59501 | 5.296 | 15.3065 | 0.21888 | 0.3192 | 1.3211 | 0.48322 | 2.4376e-06 | 23.72 | 12.65 | 49.0626 | 37.9926 | 6500 | 14.495 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.644 | 6.644 | 4.6139 | 4.6139 | 8.2025 | 0.28103 | 1.5217 | 0.59501 | 28.1375 | 88.9284 | 0.21888 | 0.3192 | 1.3211 | 0.48322 | 2.4376e-06 | 23.72 | 12.65 | 145.526 | 134.456 | 6500 | 14.495 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 6.644 | 6.644 | 4.6139 | 4.6139 | 8.2025 | 0.28103 | 1.5217 | 0.59501 | 28.1375 | 197.5945 | 0.21888 | 0.3192 | 1.3211 | 0.48322 | 2.4376e-06 | 23.72 | 12.65 | 254.1922 | 243.1222
[29 empty] | 7000 | 15.61 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.1551 | 7.1551 | 4.9688 | 4.9688 | 8.8335 | 0.32593 | 1.7648 | 0.69007 | 0.99063 | 17.752 | 0.25104 | 0.36611 | 1.5152 | 0.55422 | 2.7958e-06 | 23.72 | 12.65 | 47.93 | 36.86 | 7000 | 15.61 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.1551 | 7.1551 | 4.9688 | 4.9688 | 8.8335 | 0.32593 | 1.7648 | 0.69007 | 6.142 | 17.752 | 0.25104 | 0.36611 | 1.5152 | 0.55422 | 2.7958e-06 | 23.72 | 12.65 | 53.0814 | 42.0114 | 7000 | 15.61 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.1551 | 7.1551 | 4.9688 | 4.9688 | 8.8335 | 0.32593 | 1.7648 | 0.69007 | 32.6328 | 103.1359 | 0.25104 | 0.36611 | 1.5152 | 0.55422 | 2.7958e-06 | 23.72 | 12.65 | 164.9561 | 153.8861 | 7000 | 15.61 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.1551 | 7.1551 | 4.9688 | 4.9688 | 8.8335 | 0.32593 | 1.7648 | 0.69007 | 32.6328 | 229.1629 | 0.25104 | 0.36611 | 1.5152 | 0.55422 | 2.7958e-06 | 23.72 | 12.65 | 290.9831 | 279.9131
[29 empty] | 7500 | 16.725 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.6662 | 7.6662 | 5.3237 | 5.3237 | 9.4644 | 0.37416 | 2.0259 | 0.79217 | 1.1372 | 20.3785 | 0.28522 | 0.41595 | 1.7215 | 0.62968 | 3.1764e-06 | 23.72 | 12.65 | 51.4804 | 40.4104 | 7500 | 16.725 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.6662 | 7.6662 | 5.3237 | 5.3237 | 9.4644 | 0.37416 | 2.0259 | 0.79217 | 7.0508 | 20.3785 | 0.28522 | 0.41595 | 1.7215 | 0.62968 | 3.1764e-06 | 23.72 | 12.65 | 57.394 | 46.324 | 7500 | 16.725 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.6662 | 7.6662 | 5.3237 | 5.3237 | 9.4644 | 0.37416 | 2.0259 | 0.79217 | 37.4612 | 118.3958 | 0.28522 | 0.41595 | 1.7215 | 0.62968 | 3.1764e-06 | 23.72 | 12.65 | 185.8216 | 174.7515 | 7500 | 16.725 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 7.6662 | 7.6662 | 5.3237 | 5.3237 | 9.4644 | 0.37416 | 2.0259 | 0.79217 | 37.4612 | 263.0696 | 0.28522 | 0.41595 | 1.7215 | 0.62968 | 3.1764e-06 | 23.72 | 12.65 | 330.4954 | 319.4254
[29 empty] | 8000 | 17.84 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.1773 | 8.1773 | 5.6786 | 5.6786 | 10.0954 | 0.42571 | 2.3051 | 0.90131 | 1.2939 | 23.1862 | 0.32139 | 0.4687 | 1.9399 | 0.70953 | 3.5792e-06 | 23.72 | 12.65 | 55.2717 | 44.2017 | 8000 | 17.84 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.1773 | 8.1773 | 5.6786 | 5.6786 | 10.0954 | 0.42571 | 2.3051 | 0.90131 | 8.0223 | 23.1862 | 0.32139 | 0.4687 | 1.9399 | 0.70953 | 3.5792e-06 | 23.72 | 12.65 | 62.0001 | 50.93 | 8000 | 17.84 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.1773 | 8.1773 | 5.6786 | 5.6786 | 10.0954 | 0.42571 | 2.3051 | 0.90131 | 42.6225 | 134.7081 | 0.32139 | 0.4687 | 1.9399 | 0.70953 | 3.5792e-06 | 23.72 | 12.65 | 208.1221 | 197.0521 | 8000 | 17.84 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.1773 | 8.1773 | 5.6786 | 5.6786 | 10.0954 | 0.42571 | 2.3051 | 0.90131 | 42.6225 | 299.3148 | 0.32139 | 0.4687 | 1.9399 | 0.70953 | 3.5792e-06 | 23.72 | 12.65 | 372.7288 | 361.6588
MINOR LOSSES |  | K | qty | MINOR LOSSES |  | K | qty | MINOR LOSSES |  | K | qty | MINOR LOSSES | K | qty |  | MINOR LOSSES | K | qty |  | MINOR LOSSES | K |  | MINOR LOSSES | K |  | MINOR LOSSES | K |  | 8500 | 18.955 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.6883 | 8.6883 | 6.0336 | 6.0336 | 10.7263 | 0.48059 | 2.6022 | 1.0175 | 1.4607 | 26.1751 | 0.35954 | 0.52433 | 2.1701 | 0.79374 | 4.004e-06 | 23.72 | 12.65 | 59.3037 | 48.2337 | 8500 | 18.955 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.6883 | 8.6883 | 6.0336 | 6.0336 | 10.7263 | 0.48059 | 2.6022 | 1.0175 | 9.0564 | 26.1751 | 0.35954 | 0.52433 | 2.1701 | 0.79374 | 4.004e-06 | 23.72 | 12.65 | 66.8994 | 55.8294 | 8500 | 18.955 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.6883 | 8.6883 | 6.0336 | 6.0336 | 10.7263 | 0.48059 | 2.6022 | 1.0175 | 48.1168 | 152.0728 | 0.35954 | 0.52433 | 2.1701 | 0.79374 | 4.004e-06 | 23.72 | 12.65 | 231.8575 | 220.7875 | 8500 | 18.955 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 8.6883 | 8.6883 | 6.0336 | 6.0336 | 10.7263 | 0.48059 | 2.6022 | 1.0175 | 48.1168 | 337.8983 | 0.35954 | 0.52433 | 2.1701 | 0.79374 | 4.004e-06 | 23.72 | 12.65 | 417.6831 | 406.6131
Entry Losses |  | 0.5 | 1 | Entry Losses |  | 0.5 |  | Entry Losses |  | 0.5 |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  | Entry Losses | 0.5 |  | Entry Losses | 0.5 |  | 9000 | 20.07 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.1994 | 9.1994 | 6.3885 | 6.3885 | 11.3573 | 0.53879 | 2.9173 | 1.1407 | 1.6376 | 29.3451 | 0.39964 | 0.58281 | 2.4121 | 0.88227 | 4.4506e-06 | 23.72 | 12.65 | 63.5764 | 52.5064 | 9000 | 20.07 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.1994 | 9.1994 | 6.3885 | 6.3885 | 11.3573 | 0.53879 | 2.9173 | 1.1407 | 10.1532 | 29.3451 | 0.39964 | 0.58281 | 2.4121 | 0.88227 | 4.4506e-06 | 23.72 | 12.65 | 72.092 | 61.022 | 9000 | 20.07 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.1994 | 9.1994 | 6.3885 | 6.3885 | 11.3573 | 0.53879 | 2.9173 | 1.1407 | 53.9441 | 170.4899 | 0.39964 | 0.58281 | 2.4121 | 0.88227 | 4.4506e-06 | 23.72 | 12.65 | 257.0277 | 245.9576 | 9000 | 20.07 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.1994 | 9.1994 | 6.3885 | 6.3885 | 11.3573 | 0.53879 | 2.9173 | 1.1407 | 53.9441 | 378.8203 | 0.39964 | 0.58281 | 2.4121 | 0.88227 | 4.4506e-06 | 23.72 | 12.65 | 465.358 | 454.288
Reducer |  |  |  | Increaser |  | 0.31 | 1 | Reducer |  |  |  | Reducer | 0.5 | 0 |  | Reducer | 0.5 | 2 |  | Reducer | 0.5 | 2 | Reducer | 0.5 | 2 | Reducer | 0.5 | 2 | 9500 | 21.185 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.7105 | 9.7105 | 6.7434 | 6.7434 | 11.9883 | 0.60032 | 3.2505 | 1.271 | 1.8246 | 32.6962 | 0.44168 | 0.64412 | 2.6659 | 0.97508 | 4.9188e-06 | 23.72 | 12.65 | 68.0894 | 57.0194 | 9500 | 21.185 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.7105 | 9.7105 | 6.7434 | 6.7434 | 11.9883 | 0.60032 | 3.2505 | 1.271 | 11.3127 | 32.6962 | 0.44168 | 0.64412 | 2.6659 | 0.97508 | 4.9188e-06 | 23.72 | 12.65 | 77.5774 | 66.5074 | 9500 | 21.185 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.7105 | 9.7105 | 6.7434 | 6.7434 | 11.9883 | 0.60032 | 3.2505 | 1.271 | 60.1043 | 189.9594 | 0.44168 | 0.64412 | 2.6659 | 0.97508 | 4.9188e-06 | 23.72 | 12.65 | 283.6323 | 272.5623 | 9500 | 21.185 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 9.7105 | 9.7105 | 6.7434 | 6.7434 | 11.9883 | 0.60032 | 3.2505 | 1.271 | 60.1043 | 422.0806 | 0.44168 | 0.64412 | 2.6659 | 0.97508 | 4.9188e-06 | 23.72 | 12.65 | 515.7535 | 504.6835
Bellmouth |  | 0.05 | 1 | Bellmouth |  | 0.05 | 1 | Bellmouth |  | 0.05 |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  | Bellmouth | 0.05 |  | Bellmouth | 0.05 |  | 10000 | 22.3 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 10.2216 | 10.2216 | 7.0983 | 7.0983 | 12.6192 | 0.66517 | 3.6017 | 1.4083 | 2.0217 | 36.2285 | 0.48565 | 0.70823 | 2.9312 | 1.0721 | 5.4084e-06 | 23.72 | 12.65 | 72.8426 | 61.7726 | 10000 | 22.3 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 10.2216 | 10.2216 | 7.0983 | 7.0983 | 12.6192 | 0.66517 | 3.6017 | 1.4083 | 12.5348 | 36.2285 | 0.48565 | 0.70823 | 2.9312 | 1.0721 | 5.4084e-06 | 23.72 | 12.65 | 83.3557 | 72.2857 | 10000 | 22.3 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 10.2216 | 10.2216 | 7.0983 | 7.0983 | 12.6192 | 0.66517 | 3.6017 | 1.4083 | 66.5976 | 210.4813 | 0.48565 | 0.70823 | 2.9312 | 1.0721 | 5.4084e-06 | 23.72 | 12.65 | 311.6713 | 300.6013 | 10000 | 22.3 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 10.2216 | 10.2216 | 7.0983 | 7.0983 | 12.6192 | 0.66517 | 3.6017 | 1.4083 | 66.5976 | 467.6793 | 0.48565 | 0.70823 | 2.9312 | 1.0721 | 5.4084e-06 | 23.72 | 12.65 | 568.8693 | 557.7993
Rounded |  | 0.25 |  | Rounded |  | 0.25 |  | Rounded |  | 0.25 |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  | Rounded | 0.25 |  | Rounded | 0.25 |  | 10800 | 24.084 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.0393 | 11.0393 | 7.6662 | 7.6662 | 13.6288 | 0.77585 | 4.201 | 1.6426 | 2.3581 | 42.2569 | 0.55996 | 0.8166 | 3.3798 | 1.2362 | 6.236e-06 | 23.72 | 12.65 | 80.947 | 69.877 | 10800 | 24.084 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.0393 | 11.0393 | 7.6662 | 7.6662 | 13.6288 | 0.77585 | 4.201 | 1.6426 | 14.6206 | 42.2569 | 0.55996 | 0.8166 | 3.3798 | 1.2362 | 6.236e-06 | 23.72 | 12.65 | 93.2095 | 82.1395 | 10800 | 24.084 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.0393 | 11.0393 | 7.6662 | 7.6662 | 13.6288 | 0.77585 | 4.201 | 1.6426 | 77.6795 | 245.5054 | 0.55996 | 0.8166 | 3.3798 | 1.2362 | 6.236e-06 | 23.72 | 12.65 | 359.5169 | 348.4469 | 10800 | 24.084 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.0393 | 11.0393 | 7.6662 | 7.6662 | 13.6288 | 0.77585 | 4.201 | 1.6426 | 77.6795 | 545.5012 | 0.55996 | 0.8166 | 3.3798 | 1.2362 | 6.236e-06 | 23.72 | 12.65 | 659.5126 | 648.4426
Sharp Edged |  | 0.5 |  | Sharp Edged |  | 0.5 |  | Sharp Edged |  | 0.5 |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  | Sharp Edged | 0.5 |  | Sharp Edged | 0.5 |  | 11000 | 24.53 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.2437 | 11.2437 | 7.8081 | 7.8081 | 13.8811 | 0.80486 | 4.358 | 1.704 | 2.4463 | 43.8365 | 0.57929 | 0.8448 | 3.4965 | 1.2789 | 6.4513e-06 | 23.72 | 12.65 | 83.0691 | 71.9991 | 11000 | 24.53 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.2437 | 11.2437 | 7.8081 | 7.8081 | 13.8811 | 0.80486 | 4.358 | 1.704 | 15.1671 | 43.8365 | 0.57929 | 0.8448 | 3.4965 | 1.2789 | 6.4513e-06 | 23.72 | 12.65 | 95.7899 | 84.7199 | 11000 | 24.53 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.2437 | 11.2437 | 7.8081 | 7.8081 | 13.8811 | 0.80486 | 4.358 | 1.704 | 80.5831 | 254.6824 | 0.57929 | 0.8448 | 3.4965 | 1.2789 | 6.4513e-06 | 23.72 | 12.65 | 372.0519 | 360.9819 | 11000 | 24.53 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.2437 | 11.2437 | 7.8081 | 7.8081 | 13.8811 | 0.80486 | 4.358 | 1.704 | 80.5831 | 565.892 | 0.57929 | 0.8448 | 3.4965 | 1.2789 | 6.4513e-06 | 23.72 | 12.65 | 683.2614 | 672.1914
Projecting |  | 0.8 |  | Projecting |  | 0.8 |  | Projecting |  | 0.8 |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  | Projecting | 0.8 |  | Projecting | 0.8 |  | 11500 | 25.645 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.7548 | 11.7548 | 8.1631 | 8.1631 | 14.5121 | 0.87969 | 4.7632 | 1.8625 | 2.6737 | 47.9122 | 0.62894 | 0.91721 | 3.7961 | 1.3885 | 7.0042e-06 | 23.72 | 12.65 | 88.542 | 77.472 | 11500 | 25.645 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.7548 | 11.7548 | 8.1631 | 8.1631 | 14.5121 | 0.87969 | 4.7632 | 1.8625 | 16.5773 | 47.9122 | 0.62894 | 0.91721 | 3.7961 | 1.3885 | 7.0042e-06 | 23.72 | 12.65 | 102.4456 | 91.3756 | 11500 | 25.645 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.7548 | 11.7548 | 8.1631 | 8.1631 | 14.5121 | 0.87969 | 4.7632 | 1.8625 | 88.0753 | 278.3616 | 0.62894 | 0.91721 | 3.7961 | 1.3885 | 7.0042e-06 | 23.72 | 12.65 | 404.3931 | 393.3231 | 11500 | 25.645 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 11.7548 | 11.7548 | 8.1631 | 8.1631 | 14.5121 | 0.87969 | 4.7632 | 1.8625 | 88.0753 | 618.5059 | 0.62894 | 0.91721 | 3.7961 | 1.3885 | 7.0042e-06 | 23.72 | 12.65 | 744.5374 | 733.4674
Exit Loss |  | 1 |  | Exit Loss |  | 1 |  | Exit Loss |  | 1 |  | Exit Loss | 1 | 1 | inside building | Exit Loss | 1 |  | inside building | Exit Loss | 1 |  | Exit Loss | 1 |  | Exit Loss | 1 |  | 12000 | 26.76 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.2659 | 12.2659 | 8.518 | 8.518 | 15.1431 | 0.95785 | 5.1864 | 2.028 | 2.9113 | 52.169 | 0.68046 | 0.99234 | 4.1071 | 1.5022 | 7.578e-06 | 23.72 | 12.65 | 94.2546 | 83.1846 | 12000 | 26.76 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.2659 | 12.2659 | 8.518 | 8.518 | 15.1431 | 0.95785 | 5.1864 | 2.028 | 18.0501 | 52.169 | 0.68046 | 0.99234 | 4.1071 | 1.5022 | 7.578e-06 | 23.72 | 12.65 | 109.3935 | 98.3235 | 12000 | 26.76 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.2659 | 12.2659 | 8.518 | 8.518 | 15.1431 | 0.95785 | 5.1864 | 2.028 | 95.9006 | 303.0931 | 0.68046 | 0.99234 | 4.1071 | 1.5022 | 7.578e-06 | 23.72 | 12.65 | 438.168 | 427.098 | 12000 | 26.76 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.2659 | 12.2659 | 8.518 | 8.518 | 15.1431 | 0.95785 | 5.1864 | 2.028 | 95.9006 | 673.4582 | 0.68046 | 0.99234 | 4.1071 | 1.5022 | 7.578e-06 | 23.72 | 12.65 | 808.5332 | 797.4631
90 deg Ell, std |  | 0.36 | 1 | 90 deg Ell, std |  | 0.36 | 1 | 90 deg Ell, std |  | 0.36 | 3 | 90 deg Ell, std | 0.36 | 3 | inside building | 90 deg Ell, std | 0.36 | 2 | inside building | 90 deg Ell, std | 0.36 | 2 | 90 deg Ell, std | 0.36 | 2 | 90 deg Ell, std | 0.36 | 2 | 12500 | 27.875 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.777 | 12.777 | 8.8729 | 8.8729 | 15.774 | 1.0393 | 5.6276 | 2.2005 | 3.1589 | 56.607 | 0.73384 | 1.0702 | 4.4293 | 1.6201 | 8.1725e-06 | 23.72 | 12.65 | 100.2067 | 89.1367 | 12500 | 27.875 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.777 | 12.777 | 8.8729 | 8.8729 | 15.774 | 1.0393 | 5.6276 | 2.2005 | 19.5856 | 56.607 | 0.73384 | 1.0702 | 4.4293 | 1.6201 | 8.1725e-06 | 23.72 | 12.65 | 116.6334 | 105.5634 | 12500 | 27.875 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.777 | 12.777 | 8.8729 | 8.8729 | 15.774 | 1.0393 | 5.6276 | 2.2005 | 104.0588 | 328.8771 | 0.73384 | 1.0702 | 4.4293 | 1.6201 | 8.1725e-06 | 23.72 | 12.65 | 473.3767 | 462.3067 | 12500 | 27.875 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 12.777 | 12.777 | 8.8729 | 8.8729 | 15.774 | 1.0393 | 5.6276 | 2.2005 | 104.0588 | 730.749 | 0.73384 | 1.0702 | 4.4293 | 1.6201 | 8.1725e-06 | 23.72 | 12.65 | 875.2485 | 864.1785
45 deg Ell, std |  | 0.19 |  | 45 deg Ell, std |  | 0.19 |  | 45 deg Ell, std |  | 0.19 |  | 45 deg Ell, std | 0.19 | 0 | inside building | 45 deg Ell, std | 0.19 | 1 | inside building | 45 deg Ell, std | 0.19 | 1 | 45 deg Ell, std | 0.19 | 1 | 45 deg Ell, std | 0.19 | 1 | 13000 | 28.99 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.288 | 13.288 | 9.2278 | 9.2278 | 16.405 | 1.1241 | 6.0868 | 2.38 | 3.4167 | 61.2261 | 0.78907 | 1.1507 | 4.7626 | 1.742 | 8.7875e-06 | 23.72 | 12.65 | 106.3982 | 95.3282 | 13000 | 28.99 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.288 | 13.288 | 9.2278 | 9.2278 | 16.405 | 1.1241 | 6.0868 | 2.38 | 21.1838 | 61.2261 | 0.78907 | 1.1507 | 4.7626 | 1.742 | 8.7875e-06 | 23.72 | 12.65 | 124.1653 | 113.0953 | 13000 | 28.99 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.288 | 13.288 | 9.2278 | 9.2278 | 16.405 | 1.1241 | 6.0868 | 2.38 | 112.55 | 355.7135 | 0.78907 | 1.1507 | 4.7626 | 1.742 | 8.7875e-06 | 23.72 | 12.65 | 510.0188 | 498.9488 | 13000 | 28.99 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.288 | 13.288 | 9.2278 | 9.2278 | 16.405 | 1.1241 | 6.0868 | 2.38 | 112.55 | 790.3781 | 0.78907 | 1.1507 | 4.7626 | 1.742 | 8.7875e-06 | 23.72 | 12.65 | 944.6834 | 933.6134
Tee, line flow |  | 0.24 |  | Tee, line flow |  | 0.24 |  | Tee, line flow |  | 0.24 |  | Tee, line flow | 0.24 | 2 | inside building | Tee, line flow | 0.24 |  | inside building | Tee, line flow | 0.24 |  | Tee, line flow | 0.24 |  | Tee, line flow | 0.24 |  | 13500 | 30.105 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.7991 | 13.7991 | 9.5827 | 9.5827 | 17.0359 | 1.2123 | 6.564 | 2.5666 | 3.6846 | 66.0264 | 0.84613 | 1.2339 | 5.107 | 1.868 | 9.4229e-06 | 23.72 | 12.65 | 112.829 | 101.759 | 13500 | 30.105 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.7991 | 13.7991 | 9.5827 | 9.5827 | 17.0359 | 1.2123 | 6.564 | 2.5666 | 22.8447 | 66.0264 | 0.84613 | 1.2339 | 5.107 | 1.868 | 9.4229e-06 | 23.72 | 12.65 | 131.9891 | 120.9191 | 13500 | 30.105 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.7991 | 13.7991 | 9.5827 | 9.5827 | 17.0359 | 1.2123 | 6.564 | 2.5666 | 121.3741 | 383.6022 | 0.84613 | 1.2339 | 5.107 | 1.868 | 9.4229e-06 | 23.72 | 12.65 | 548.0944 | 537.0244 | 13500 | 30.105 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 13.7991 | 13.7991 | 9.5827 | 9.5827 | 17.0359 | 1.2123 | 6.564 | 2.5666 | 121.3741 | 852.3456 | 0.84613 | 1.2339 | 5.107 | 1.868 | 9.4229e-06 | 23.72 | 12.65 | 1016.8377 | 1005.7677
Tee, branch flow |  | 0.72 | 0 | Tee, branch flow |  | 0.72 | 0 | Tee, branch flow |  | 0.72 | 1 | Tee, branch flow | 0.72 | 1 | inside building | Tee, branch flow | 0.72 |  | inside building | Tee, branch flow | 0.72 |  | Tee, branch flow | 0.72 |  | Tee, branch flow | 0.72 |  | 14000 | 31.22 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.3102 | 14.3102 | 9.9376 | 9.9376 | 17.6669 | 1.3037 | 7.0592 | 2.7603 | 3.9625 | 71.0078 | 0.90502 | 1.3198 | 5.4625 | 1.998 | 1.0079e-05 | 23.72 | 12.65 | 119.4989 | 108.4289 | 14000 | 31.22 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.3102 | 14.3102 | 9.9376 | 9.9376 | 17.6669 | 1.3037 | 7.0592 | 2.7603 | 24.5682 | 71.0078 | 0.90502 | 1.3198 | 5.4625 | 1.998 | 1.0079e-05 | 23.72 | 12.65 | 140.1046 | 129.0345 | 14000 | 31.22 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.3102 | 14.3102 | 9.9376 | 9.9376 | 17.6669 | 1.3037 | 7.0592 | 2.7603 | 130.5313 | 412.5434 | 0.90502 | 1.3198 | 5.4625 | 1.998 | 1.0079e-05 | 23.72 | 12.65 | 587.6033 | 576.5333 | 14000 | 31.22 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.3102 | 14.3102 | 9.9376 | 9.9376 | 17.6669 | 1.3037 | 7.0592 | 2.7603 | 130.5313 | 916.6515 | 0.90502 | 1.3198 | 5.4625 | 1.998 | 1.0079e-05 | 23.72 | 12.65 | 1091.7113 | 1080.6413
Coupling |  | 0.04 |  | Coupling |  | 0.04 |  | Coupling |  | 0.04 |  | Coupling | 0.04 |  | inside building | Coupling | 0.04 |  | inside building | Coupling | 0.04 |  | Coupling | 0.04 |  | Coupling | 0.04 |  | 14500 | 32.335 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.8213 | 14.8213 | 10.2926 | 10.2926 | 18.2979 | 1.3985 | 7.5725 | 2.961 | 4.2506 | 76.1704 | 0.96572 | 1.4083 | 5.8289 | 2.132 | 1.0755e-05 | 23.72 | 12.65 | 126.4079 | 115.3379 | 14500 | 32.335 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.8213 | 14.8213 | 10.2926 | 10.2926 | 18.2979 | 1.3985 | 7.5725 | 2.961 | 26.3544 | 76.1704 | 0.96572 | 1.4083 | 5.8289 | 2.132 | 1.0755e-05 | 23.72 | 12.65 | 148.5116 | 137.4416 | 14500 | 32.335 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.8213 | 14.8213 | 10.2926 | 10.2926 | 18.2979 | 1.3985 | 7.5725 | 2.961 | 140.0215 | 442.537 | 0.96572 | 1.4083 | 5.8289 | 2.132 | 1.0755e-05 | 23.72 | 12.65 | 628.5453 | 617.4753 | 14500 | 32.335 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 14.8213 | 14.8213 | 10.2926 | 10.2926 | 18.2979 | 1.3985 | 7.5725 | 2.961 | 140.0215 | 983.2958 | 0.96572 | 1.4083 | 5.8289 | 2.132 | 1.0755e-05 | 23.72 | 12.65 | 1169.3041 | 1158.2341
Union |  | 0.04 |  | Union |  | 0.04 |  | Union |  | 0.04 |  | Union | 0.04 | 0 | inside building | Union | 0.04 |  | inside building | Union | 0.04 |  | Union | 0.04 |  | Union | 0.04 |  | 15000 | 33.45 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.3324 | 15.3324 | 10.6475 | 10.6475 | 18.9288 | 1.4966 | 8.1037 | 3.1687 | 4.5488 | 81.5141 | 1.0282 | 1.4995 | 6.2061 | 2.27 | 1.1451e-05 | 23.72 | 12.65 | 133.5558 | 122.4858 | 15000 | 33.45 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.3324 | 15.3324 | 10.6475 | 10.6475 | 18.9288 | 1.4966 | 8.1037 | 3.1687 | 28.2033 | 81.5141 | 1.0282 | 1.4995 | 6.2061 | 2.27 | 1.1451e-05 | 23.72 | 12.65 | 157.2102 | 146.1402 | 15000 | 33.45 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.3324 | 15.3324 | 10.6475 | 10.6475 | 18.9288 | 1.4966 | 8.1037 | 3.1687 | 149.8446 | 473.583 | 1.0282 | 1.4995 | 6.2061 | 2.27 | 1.1451e-05 | 23.72 | 12.65 | 670.9205 | 659.8505 | 15000 | 33.45 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.3324 | 15.3324 | 10.6475 | 10.6475 | 18.9288 | 1.4966 | 8.1037 | 3.1687 | 149.8446 | 1052.2785 | 1.0282 | 1.4995 | 6.2061 | 2.27 | 1.1451e-05 | 23.72 | 12.65 | 1249.616 | 1238.546
Butterfly Valve, Open |  | 0.3 |  | Butterfly Valve, Open |  | 0.3 | 1 | Butterfly Valve, Open |  | 0.3 |  | Butterfly Valve, Open | 12.7411 | 1 |  | Butterfly Valve, 50% Open | 12.7411 | 1 |  | Butterfly Valve, 27.5% Open | 83.2106 | 1 | Butterfly Valve, 20% Open | 187.2238 | 1 | Butterfly Valve, 70% Open | 0.67401 | 1 | 15500 | 34.565 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.8434 | 15.8434 | 11.0024 | 11.0024 | 19.5598 | 1.5981 | 8.653 | 3.3835 | 4.8571 | 87.0389 | 1.0925 | 1.5933 | 6.5943 | 2.4119 | 1.2167e-05 | 23.72 | 12.65 | 140.9426 | 129.8726 | 15500 | 34.565 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.8434 | 15.8434 | 11.0024 | 11.0024 | 19.5598 | 1.5981 | 8.653 | 3.3835 | 30.1148 | 87.0389 | 1.0925 | 1.5933 | 6.5943 | 2.4119 | 1.2167e-05 | 23.72 | 12.65 | 166.2003 | 155.1303 | 15500 | 34.565 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.8434 | 15.8434 | 11.0024 | 11.0024 | 19.5598 | 1.5981 | 8.653 | 3.3835 | 160.0008 | 505.6814 | 1.0925 | 1.5933 | 6.5943 | 2.4119 | 1.2167e-05 | 23.72 | 12.65 | 714.7287 | 703.6587 | 15500 | 34.565 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 15.8434 | 15.8434 | 11.0024 | 11.0024 | 19.5598 | 1.5981 | 8.653 | 3.3835 | 160.0008 | 1123.5996 | 1.0925 | 1.5933 | 6.5943 | 2.4119 | 1.2167e-05 | 23.72 | 12.65 | 1332.6469 | 1321.5768
Gate Valve, open |  | 0.1 |  | Gate Valve, open |  | 0.1 |  | Gate Valve, open |  | 0.1 |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  | Gate Valve, open | 0.1 |  | Gate Valve, open | 0.1 |  | 16000 | 35.68 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.3545 | 16.3545 | 11.3573 | 11.3573 | 20.1907 | 1.7028 | 9.2202 | 3.6053 | 5.1756 | 92.7449 | 1.1586 | 1.6897 | 6.9932 | 2.5579 | 1.2903e-05 | 23.72 | 12.65 | 148.5681 | 137.4981 | 16000 | 35.68 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.3545 | 16.3545 | 11.3573 | 11.3573 | 20.1907 | 1.7028 | 9.2202 | 3.6053 | 32.0891 | 92.7449 | 1.1586 | 1.6897 | 6.9932 | 2.5579 | 1.2903e-05 | 23.72 | 12.65 | 175.4816 | 164.4116 | 16000 | 35.68 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.3545 | 16.3545 | 11.3573 | 11.3573 | 20.1907 | 1.7028 | 9.2202 | 3.6053 | 170.4899 | 538.8322 | 1.1586 | 1.6897 | 6.9932 | 2.5579 | 1.2903e-05 | 23.72 | 12.65 | 759.9697 | 748.8997 | 16000 | 35.68 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.3545 | 16.3545 | 11.3573 | 11.3573 | 20.1907 | 1.7028 | 9.2202 | 3.6053 | 170.4899 | 1197.2591 | 1.1586 | 1.6897 | 6.9932 | 2.5579 | 1.2903e-05 | 23.72 | 12.65 | 1418.3966 | 1407.3266
Cross, line flow |  | 0.5 |  | Cross, line flow |  | 0.5 |  | Cross, line flow |  | 0.5 |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  | Cross, line flow | 0.5 |  | Cross, line flow | 0.5 |  | 16500 | 36.795 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.8656 | 16.8656 | 11.7122 | 11.7122 | 20.8217 | 1.8109 | 9.8055 | 3.8341 | 5.5041 | 98.632 | 1.2265 | 1.7886 | 7.4028 | 2.7077 | 1.3659e-05 | 23.72 | 12.65 | 156.4323 | 145.3623 | 16500 | 36.795 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.8656 | 16.8656 | 11.7122 | 11.7122 | 20.8217 | 1.8109 | 9.8055 | 3.8341 | 34.126 | 98.632 | 1.2265 | 1.7886 | 7.4028 | 2.7077 | 1.3659e-05 | 23.72 | 12.65 | 185.0542 | 173.9842 | 16500 | 36.795 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.8656 | 16.8656 | 11.7122 | 11.7122 | 20.8217 | 1.8109 | 9.8055 | 3.8341 | 181.312 | 573.0354 | 1.2265 | 1.7886 | 7.4028 | 2.7077 | 1.3659e-05 | 23.72 | 12.65 | 806.6436 | 795.5736 | 16500 | 36.795 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 16.8656 | 16.8656 | 11.7122 | 11.7122 | 20.8217 | 1.8109 | 9.8055 | 3.8341 | 181.312 | 1273.257 | 1.2265 | 1.7886 | 7.4028 | 2.7077 | 1.3659e-05 | 23.72 | 12.65 | 1506.8652 | 1495.7952
Cross, branch flow |  | 0.75 |  | Cross, branch flow |  | 0.75 |  | Cross, branch flow |  | 0.75 |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  | Cross, branch flow | 0.75 |  | Cross, branch flow | 0.75 |  | 17000 | 37.91 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.3767 | 17.3767 | 12.0671 | 12.0671 | 21.4527 | 1.9223 | 10.4088 | 4.07 | 5.8427 | 104.7003 | 1.2961 | 1.8902 | 7.8232 | 2.8614 | 1.4434e-05 | 23.72 | 12.65 | 164.5351 | 153.4651 | 17000 | 37.91 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.3767 | 17.3767 | 12.0671 | 12.0671 | 21.4527 | 1.9223 | 10.4088 | 4.07 | 36.2256 | 104.7003 | 1.2961 | 1.8902 | 7.8232 | 2.8614 | 1.4434e-05 | 23.72 | 12.65 | 194.9179 | 183.8479 | 17000 | 37.91 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.3767 | 17.3767 | 12.0671 | 12.0671 | 21.4527 | 1.9223 | 10.4088 | 4.07 | 192.4671 | 608.2911 | 1.2961 | 1.8902 | 7.8232 | 2.8614 | 1.4434e-05 | 23.72 | 12.65 | 854.7502 | 843.6802 | 17000 | 37.91 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.3767 | 17.3767 | 12.0671 | 12.0671 | 21.4527 | 1.9223 | 10.4088 | 4.07 | 192.4671 | 1351.5933 | 1.2961 | 1.8902 | 7.8232 | 2.8614 | 1.4434e-05 | 23.72 | 12.65 | 1598.0524 | 1586.9824
Wye |  | 0.5 |  | Wye |  | 0.5 |  | Wye |  | 0.5 |  | Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  | Wye | 0.5 |  | Wye | 0.5 |  | 17500 | 39.025 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.8877 | 17.8877 | 12.422 | 12.422 | 22.0836 | 2.0371 | 11.0301 | 4.3129 | 6.1915 | 110.9497 | 1.3675 | 1.9943 | 8.2542 | 3.0191 | 1.523e-05 | 23.72 | 12.65 | 172.8764 | 161.8064 | 17500 | 39.025 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.8877 | 17.8877 | 12.422 | 12.422 | 22.0836 | 2.0371 | 11.0301 | 4.3129 | 38.3878 | 110.9497 | 1.3675 | 1.9943 | 8.2542 | 3.0191 | 1.523e-05 | 23.72 | 12.65 | 205.0727 | 194.0027 | 17500 | 39.025 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.8877 | 17.8877 | 12.422 | 12.422 | 22.0836 | 2.0371 | 11.0301 | 4.3129 | 203.9552 | 644.5991 | 1.3675 | 1.9943 | 8.2542 | 3.0191 | 1.523e-05 | 23.72 | 12.65 | 904.2895 | 893.2195 | 17500 | 39.025 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 17.8877 | 17.8877 | 12.422 | 12.422 | 22.0836 | 2.0371 | 11.0301 | 4.3129 | 203.9552 | 1432.268 | 1.3675 | 1.9943 | 8.2542 | 3.0191 | 1.523e-05 | 23.72 | 12.65 | 1691.9583 | 1680.8883
Ball Check Valve |  | 0.66 |  | Ball Check Valve |  | 0.66 |  | Ball Check Valve |  | 0.66 |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  | Ball Check Valve | 0.66 |  | Ball Check Valve | 0.66 |  | 18000 | 40.14 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.3988 | 18.3988 | 12.777 | 12.777 | 22.7146 | 2.1552 | 11.6694 | 4.5629 | 6.5503 | 117.3803 | 1.4407 | 2.101 | 8.6957 | 3.1806 | 1.6044e-05 | 23.72 | 12.65 | 181.4561 | 170.3861 | 18000 | 40.14 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.3988 | 18.3988 | 12.777 | 12.777 | 22.7146 | 2.1552 | 11.6694 | 4.5629 | 40.6127 | 117.3803 | 1.4407 | 2.101 | 8.6957 | 3.1806 | 1.6044e-05 | 23.72 | 12.65 | 215.5185 | 204.4485 | 18000 | 40.14 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.3988 | 18.3988 | 12.777 | 12.777 | 22.7146 | 2.1552 | 11.6694 | 4.5629 | 215.7763 | 681.9595 | 1.4407 | 2.101 | 8.6957 | 3.1806 | 1.6044e-05 | 23.72 | 12.65 | 955.2613 | 944.1913 | 18000 | 40.14 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.3988 | 18.3988 | 12.777 | 12.777 | 22.7146 | 2.1552 | 11.6694 | 4.5629 | 215.7763 | 1515.281 | 1.4407 | 2.101 | 8.6957 | 3.1806 | 1.6044e-05 | 23.72 | 12.65 | 1788.5828 | 1777.5128
Rubber swingcheck valve |  | 1.2 |  | Rubber swingcheck valve |  | 1.2 |  | Rubber swingcheck valve |  | 1.2 |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  | Rubber swingcheck valve | 1.2 |  | Rubber swingcheck valve | 1.2 |  | 18500 | 41.255 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.9099 | 18.9099 | 13.1319 | 13.1319 | 23.3456 | 2.2765 | 12.3267 | 4.8199 | 6.9193 | 123.992 | 1.5156 | 2.2103 | 9.1479 | 3.346 | 1.6879e-05 | 23.72 | 12.65 | 190.2741 | 179.2041 | 18500 | 41.255 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.9099 | 18.9099 | 13.1319 | 13.1319 | 23.3456 | 2.2765 | 12.3267 | 4.8199 | 42.9003 | 123.992 | 1.5156 | 2.2103 | 9.1479 | 3.346 | 1.6879e-05 | 23.72 | 12.65 | 226.2551 | 215.1851 | 18500 | 41.255 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.9099 | 18.9099 | 13.1319 | 13.1319 | 23.3456 | 2.2765 | 12.3267 | 4.8199 | 227.9303 | 720.3724 | 1.5156 | 2.2103 | 9.1479 | 3.346 | 1.6879e-05 | 23.72 | 12.65 | 1007.6655 | 996.5955 | 18500 | 41.255 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 18.9099 | 18.9099 | 13.1319 | 13.1319 | 23.3456 | 2.2765 | 12.3267 | 4.8199 | 227.9303 | 1600.6325 | 1.5156 | 2.2103 | 9.1479 | 3.346 | 1.6879e-05 | 23.72 | 12.65 | 1887.9257 | 1876.8557
Metal swing check valve |  | 1.2 |  | Metal swing check valve |  | 1.2 | 1 | Metal swing check valve |  | 1.2 |  | Metal swing check valve | 1.2 |  |  | Metal swing check valve | 1.2 |  |  | Metal swing check valve | 1.2 |  | Metal swing check valve | 1.2 |  | Metal swing check valve | 1.2 |  | 19000 | 42.37 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.421 | 19.421 | 13.4868 | 13.4868 | 23.9765 | 2.4013 | 13.002 | 5.084 | 7.2984 | 130.7848 | 1.5923 | 2.322 | 9.6105 | 3.5152 | 1.7732e-05 | 23.72 | 12.65 | 199.3304 | 188.2604 | 19000 | 42.37 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.421 | 19.421 | 13.4868 | 13.4868 | 23.9765 | 2.4013 | 13.002 | 5.084 | 45.2506 | 130.7848 | 1.5923 | 2.322 | 9.6105 | 3.5152 | 1.7732e-05 | 23.72 | 12.65 | 237.2826 | 226.2126 | 19000 | 42.37 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.421 | 19.421 | 13.4868 | 13.4868 | 23.9765 | 2.4013 | 13.002 | 5.084 | 240.4174 | 759.8376 | 1.5923 | 2.322 | 9.6105 | 3.5152 | 1.7732e-05 | 23.72 | 12.65 | 1061.5022 | 1050.4322 | 19000 | 42.37 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.421 | 19.421 | 13.4868 | 13.4868 | 23.9765 | 2.4013 | 13.002 | 5.084 | 240.4174 | 1688.3224 | 1.5923 | 2.322 | 9.6105 | 3.5152 | 1.7732e-05 | 23.72 | 12.65 | 1989.987 | 1978.917
Gate Valve |  | 0.1 |  | Gate Valve |  | 0.1 |  | Gate Valve |  | 0.1 |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  | Gate Valve | 0.1 |  | Gate Valve | 0.1 |  | 19500 | 43.485 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.9321 | 19.9321 | 13.8417 | 13.8417 | 24.6075 | 2.5293 | 13.6953 | 5.3551 | 7.6875 | 137.7588 | 1.6706 | 2.4364 | 10.0836 | 3.6882 | 1.8605e-05 | 23.72 | 12.65 | 208.6249 | 197.5548 | 19500 | 43.485 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.9321 | 19.9321 | 13.8417 | 13.8417 | 24.6075 | 2.5293 | 13.6953 | 5.3551 | 47.6636 | 137.7588 | 1.6706 | 2.4364 | 10.0836 | 3.6882 | 1.8605e-05 | 23.72 | 12.65 | 248.6009 | 237.5309 | 19500 | 43.485 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.9321 | 19.9321 | 13.8417 | 13.8417 | 24.6075 | 2.5293 | 13.6953 | 5.3551 | 253.2374 | 800.3553 | 1.6706 | 2.4364 | 10.0836 | 3.6882 | 1.8605e-05 | 23.72 | 12.65 | 1116.7712 | 1105.7012 | 19500 | 43.485 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 19.9321 | 19.9321 | 13.8417 | 13.8417 | 24.6075 | 2.5293 | 13.6953 | 5.3551 | 253.2374 | 1778.3507 | 1.6706 | 2.4364 | 10.0836 | 3.6882 | 1.8605e-05 | 23.72 | 12.65 | 2094.7666 | 2083.6966
Ball Valve |  | 0..04 |  | Ball Valve |  | 0..04 |  | Ball Valve |  | 0..04 |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  | Ball Valve | 0.04 |  | Ball Valve | 0.04 |  | 20000 | 44.6 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.4431 | 20.4431 | 14.1966 | 14.1966 | 25.2384 | 2.6607 | 14.4066 | 5.6332 | 8.0868 | 144.9139 | 1.7508 | 2.5532 | 10.5671 | 3.8651 | 1.9497e-05 | 23.72 | 12.65 | 218.1574 | 207.0874 | 20000 | 44.6 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.4431 | 20.4431 | 14.1966 | 14.1966 | 25.2384 | 2.6607 | 14.4066 | 5.6332 | 50.1392 | 144.9139 | 1.7508 | 2.5532 | 10.5671 | 3.8651 | 1.9497e-05 | 23.72 | 12.65 | 260.2098 | 249.1398 | 20000 | 44.6 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.4431 | 20.4431 | 14.1966 | 14.1966 | 25.2384 | 2.6607 | 14.4066 | 5.6332 | 266.3904 | 841.9253 | 1.7508 | 2.5532 | 10.5671 | 3.8651 | 1.9497e-05 | 23.72 | 12.65 | 1173.4725 | 1162.4025 | 20000 | 44.6 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.4431 | 20.4431 | 14.1966 | 14.1966 | 25.2384 | 2.6607 | 14.4066 | 5.6332 | 266.3904 | 1870.7173 | 1.7508 | 2.5532 | 10.5671 | 3.8651 | 1.9497e-05 | 23.72 | 12.65 | 2202.2645 | 2191.1944
TOTAL K IN APP |  | 0.41 |  | TOTAL K IN APP |  | 2.22 |  | TOTAL K IN APP |  | 1.8 |  | TOTAL K IN APP | 16.0211 |  |  | TOTAL K IN APP | 14.6511 |  |  | TOTAL K IN APP | 85.1206 |  | TOTAL K IN APP | 189.1338 |  | TOTAL K IN APP | 2.584 |  | 20500 | 45.715 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.9542 | 20.9542 | 14.5515 | 14.5515 | 25.8694 | 2.7954 | 15.136 | 5.9184 | 8.4962 | 152.2502 | 1.8326 | 2.6725 | 11.0611 | 4.0457 | 2.0409e-05 | 23.72 | 12.65 | 227.9281 | 216.858 | 20500 | 45.715 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.9542 | 20.9542 | 14.5515 | 14.5515 | 25.8694 | 2.7954 | 15.136 | 5.9184 | 52.6775 | 152.2502 | 1.8326 | 2.6725 | 11.0611 | 4.0457 | 2.0409e-05 | 23.72 | 12.65 | 272.1093 | 261.0393 | 20500 | 45.715 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.9542 | 20.9542 | 14.5515 | 14.5515 | 25.8694 | 2.7954 | 15.136 | 5.9184 | 279.8765 | 884.5478 | 1.8326 | 2.6725 | 11.0611 | 4.0457 | 2.0409e-05 | 23.72 | 12.65 | 1231.6059 | 1220.5359 | 20500 | 45.715 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 20.9542 | 20.9542 | 14.5515 | 14.5515 | 25.8694 | 2.7954 | 15.136 | 5.9184 | 279.8765 | 1965.4224 | 1.8326 | 2.6725 | 11.0611 | 4.0457 | 2.0409e-05 | 23.72 | 12.65 | 2312.4805 | 2301.4105
[29 empty] | 21000 | 46.83 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.4653 | 21.4653 | 14.9065 | 14.9065 | 26.5004 | 2.9334 | 15.8833 | 6.2106 | 8.9157 | 159.7676 | 1.9161 | 2.7944 | 11.5653 | 4.2302 | 2.1339e-05 | 23.72 | 12.65 | 237.9366 | 226.8666 | 21000 | 46.83 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.4653 | 21.4653 | 14.9065 | 14.9065 | 26.5004 | 2.9334 | 15.8833 | 6.2106 | 55.2784 | 159.7676 | 1.9161 | 2.7944 | 11.5653 | 4.2302 | 2.1339e-05 | 23.72 | 12.65 | 284.2994 | 273.2293 | 21000 | 46.83 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.4653 | 21.4653 | 14.9065 | 14.9065 | 26.5004 | 2.9334 | 15.8833 | 6.2106 | 293.6955 | 928.2227 | 1.9161 | 2.7944 | 11.5653 | 4.2302 | 2.1339e-05 | 23.72 | 12.65 | 1291.1715 | 1280.1015 | 21000 | 46.83 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.4653 | 21.4653 | 14.9065 | 14.9065 | 26.5004 | 2.9334 | 15.8833 | 6.2106 | 293.6955 | 2062.4658 | 1.9161 | 2.7944 | 11.5653 | 4.2302 | 2.1339e-05 | 23.72 | 12.65 | 2425.4146 | 2414.3446
[20 empty] | Brian to Review outside the Building Fittings |  |  | Brian to Review outside the Building Fittings |  |  | Brian to Review outside the Building Fittings |  |  | 21500 | 47.945 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.9764 | 21.9764 | 15.2614 | 15.2614 | 27.1313 | 3.0748 | 16.6486 | 6.5099 | 9.3453 | 167.4661 | 2.0014 | 2.9187 | 12.0799 | 4.4184 | 2.2288e-05 | 23.72 | 12.65 | 248.1831 | 237.1131 | 21500 | 47.945 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.9764 | 21.9764 | 15.2614 | 15.2614 | 27.1313 | 3.0748 | 16.6486 | 6.5099 | 57.9421 | 167.4661 | 2.0014 | 2.9187 | 12.0799 | 4.4184 | 2.2288e-05 | 23.72 | 12.65 | 296.7799 | 285.7099 | 21500 | 47.945 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.9764 | 21.9764 | 15.2614 | 15.2614 | 27.1313 | 3.0748 | 16.6486 | 6.5099 | 307.8475 | 972.95 | 2.0014 | 2.9187 | 12.0799 | 4.4184 | 2.2288e-05 | 23.72 | 12.65 | 1352.1691 | 1341.0991 | 21500 | 47.945 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 21.9764 | 21.9764 | 15.2614 | 15.2614 | 27.1313 | 3.0748 | 16.6486 | 6.5099 | 307.8475 | 2161.8477 | 2.0014 | 2.9187 | 12.0799 | 4.4184 | 2.2288e-05 | 23.72 | 12.65 | 2541.0668 | 2529.9968
[29 empty] | 22000 | 49.06 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 22.4874 | 22.4874 | 15.6163 | 15.6163 | 27.7623 | 3.2194 | 17.432 | 6.8162 | 9.785 | 175.3458 | 2.0883 | 3.0455 | 12.6047 | 4.6104 | 2.3257e-05 | 23.72 | 12.65 | 258.6675 | 247.5975 | 22000 | 49.06 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 22.4874 | 22.4874 | 15.6163 | 15.6163 | 27.7623 | 3.2194 | 17.432 | 6.8162 | 60.6684 | 175.3458 | 2.0883 | 3.0455 | 12.6047 | 4.6104 | 2.3257e-05 | 23.72 | 12.65 | 309.5508 | 298.4808 | 22000 | 49.06 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 22.4874 | 22.4874 | 15.6163 | 15.6163 | 27.7623 | 3.2194 | 17.432 | 6.8162 | 322.3324 | 1018.7297 | 2.0883 | 3.0455 | 12.6047 | 4.6104 | 2.3257e-05 | 23.72 | 12.65 | 1414.5987 | 1403.5287 | 22000 | 49.06 | 2.1817 | 2.1817 | 3.1416 | 3.1416 | 1.7671 | 22.4874 | 22.4874 | 15.6163 | 15.6163 | 27.7623 | 3.2194 | 17.432 | 6.8162 | 322.3324 | 1018.7297 | 2.0883 | 3.0455 | 12.6047 | 4.6104 | 2.3257e-05 | 23.72 | 12.65 | 1414.5987 | 1403.5287
Modulating BFV K Value Calculation
K= (894 x d^4) / (Cv^2)
K @50% Open |  |  |  | K @ 27.5% Open |  |  |  | K @ 20% Open
d= | 18 | inches |  | d= | 18 |  |  | d= | 18
CV | 11800 |  |  | CV | 11800 |  |  | CV | 11800
%Cv/Kv | 23% |  |  | %Cv/Kv | 9% |  |  | %Cv/Kv | 6%
Weighted Cv | 2714 |  |  | Weighted Cv | 1062 |  |  | Weighted Cv | 708
K | 12.7411 |  |  | K | 83.2106 |  |  | K | 187.2238
K@100% Open
Cv | 11800
%CV/Kv | 100%
Cv | 11800 |  |  | K @ 100 Open
K | 0.67401 |  |  | d= | 18 |  |  | Cv's shown from HP BFV
|  |  |  | CV | 11800
Dezurik BFV Catalogue |  |  |  | %Cv/Kv | 100%
|  |  |  | Weighted Cv | 11800
|  |  |  | K | 0.67401
Standard Dezurik BFV | [21 empty] | High Performance Dezurik BFV
Note on C31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on H31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on L31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on Q31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on V31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on AA31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on AF31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on AJ31: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4

## Leopold Curve
| Flow | Flow | Duration | Volume
| gpm/sf | gpm | MIN | Gal
Surface Wash Flow | 0 |  | 0 | 0
Wash Ramp Up | 3 | 1800 | 1 | 1800
Wash Flow | 9 | 5400 | 1 | 5400
Hi Wash Flow | 18 | 10800 | 10 | 108000
Wash Ramp Down | 9 | 5400 | 1.5 | 8100
Wash Ramp Down | 5 | 3000 | 1.5 | 4500
Total |  |  | 15 | 126000