## Pump Info
Large Pump info from Manufacturers Curve |  |  |  | Set Points
Pressure Head (ft) |  |  |  | Qhigh rate, new filters |  | 10800 | gpm
Flow (gpm)
| 1 Pump | 2 Pump
104 | 0 | 0
94 | 1000 | 2000
86 | 2000 | 4000
79 | 3000 | 6000
72 | 4000 | 8000
68 | 5000 | 10000
64 | 6000 | 12000
62 | 7000 | 14000
58 | 8000 | 16000
56 | 8600 | 17200
52 | 9000 | 18000
43 | 10000 | 20000
32 | 11000 | 22000
28 | 11200 | 22400
Pressure Head (ft) |  |  |  | Flow (gpm)
Flow (gpm)
|  |  |  | 1 Pump | 2 Pump
|  |  |  | 0 | 0
|  |  |  | 1000 | 2000
|  |  |  | 2000 | 4000
|  |  |  | 3000 | 6000
|  |  |  | 4000 | 8000
|  |  |  | 5000 | 10000
|  |  |  | 6000 | 12000
|  |  |  | 7000 | 14000
|  |  |  | 8000 | 16000
|  |  |  | 8600 | 17200
|  |  |  | 9000 | 18000
|  |  |  | 10000 | 20000
60 hz | 50 hz | 40 hz | 35 hz | 1 Pump | 2 Pump
104 | 94.9386 | 84.9156 | 79.4313 | 0 | 0
94 | 85.8099 | 76.7507 | 71.7937 | 1000 | 2000
86 | 78.5069 | 70.2187 | 65.6836 | 2000 | 4000
79 | 72.1168 | 64.5032 | 60.3372 | 3000 | 6000
72 | 65.7267 | 58.7878 | 54.9909 | 4000 | 8000
68 | 62.0752 | 55.5218 | 51.9359 | 5000 | 10000
64 | 58.4237 | 52.2558 | 48.8808 | 6000 | 12000
62 | 56.598 | 50.6228 | 47.3533 | 7000 | 14000
58 | 52.9465 | 47.3568 | 44.2982 | 8000 | 16000
56 | 51.1208 | 45.7238 | 42.7707 | 8600 | 17200
52 | 47.4693 | 42.4578 | 39.7157 | 9000 | 18000
43 | 39.2534 | 35.1094 | 32.8418 | 10000 | 20000
32 | 29.2119 | 26.1279 | 24.4404 | 11000 | 22000
28 | 25.5604 | 22.8619 | 21.3854 | 11200 | 22400

## BWR Sys Curve - Existing
SYSTEM CURVE
| Min. Wet Well WSE | 5176.23 | Current pump 1 on depth |  |  |  | Existing Set Points in Wetwell
| Max. Wet Well EL | 5180.01 | OVF |  |  |  | Low | 5 | ft
| Min Exit EL | 5190.07 | To be confirmed with 2004 B&C Drawings |  |  |  | High Alarm | 10 | ft
| Max Exit El | 5196.32 |  |  |  |  | High High | 10.2 | ft
STATIC HEAD | [14 empty] | Flow |  | Seg 1 Area | Seg 2 Area | Seg 3 Area | Seg 4 Area | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Seg 4 Velocity | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Seg 4 h_minor | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | Seg 4 h_friction | h_minor total | h_friction total | h_delta_max | h_delta_min | TDH Max | TDH Min
Max. Total Static Head |  | 20.09 | [12 empty] | gpm | cfs | sf | sf | sf | sf | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft
Min Total Static Head |  | 10.06 | [12 empty] | 0 | 0 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.09 | 10.06 | 20.09 | 10.06
[15 empty] | 500 | 1.115 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 0.51108 | 0.35492 | 0.51108 | 0.51108 | 0.011884 | 0.00070415 | 0.0052321 | 0.0026769 | 0.00080998 | 0.0018159 | 0.15894 | 0.010183 | 0.020497 | 0.17174 | 20.09 | 10.06 | 20.2822 | 10.2522
FRICTION LOSS |  | C_water | C_wastewater | [11 empty] | 1000 | 2.23 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 1.0222 | 0.70983 | 1.0222 | 1.0222 | 0.047535 | 0.0028166 | 0.020929 | 0.010708 | 0.00292 | 0.0065462 | 0.57296 | 0.03671 | 0.081988 | 0.61914 | 20.09 | 10.06 | 20.7911 | 10.7611
Hazen Williams Coefficients |  | 80-120 | 80-110 | [11 empty] | 1500 | 3.345 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 1.5332 | 1.0647 | 1.5332 | 1.5332 | 0.10695 | 0.0063374 | 0.047089 | 0.024092 | 0.0061823 | 0.01386 | 1.2131 | 0.077723 | 0.18447 | 1.3109 | 20.09 | 10.06 | 21.5853 | 11.5553
DI |  | 110-130 | 110-130 | [11 empty] | 2000 | 4.46 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 2.0443 | 1.4197 | 2.0443 | 2.0443 | 0.19014 | 0.011266 | 0.083714 | 0.04283 | 0.010527 | 0.023599 | 2.0655 | 0.13234 | 0.32795 | 2.232 | 20.09 | 10.06 | 22.65 | 12.62
Steel |  | 135-150 | 130-145 | [11 empty] | 2500 | 5.575 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 2.5554 | 1.7746 | 2.5554 | 2.5554 | 0.2971 | 0.017604 | 0.1308 | 0.066923 | 0.015906 | 0.03566 | 3.1212 | 0.19997 | 0.51243 | 3.3727 | 20.09 | 10.06 | 23.9751 | 13.9451
PVC | [14 empty] | 3000 | 6.69 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 3.0665 | 2.1295 | 3.0665 | 3.0665 | 0.42782 | 0.025349 | 0.18836 | 0.096369 | 0.022287 | 0.049965 | 4.3732 | 0.28019 | 0.73789 | 4.7257 | 20.09 | 10.06 | 25.5536 | 15.5236
[15 empty] | 3500 | 7.805 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 3.5775 | 2.4844 | 3.5775 | 3.5775 | 0.58231 | 0.034503 | 0.25637 | 0.13117 | 0.029642 | 0.066453 | 5.8164 | 0.37265 | 1.0044 | 6.2851 | 20.09 | 10.06 | 27.3795 | 17.3495
Segment 1 (Pump Suction Pipe) |  |  |  | Segment 2 (Pump Discharge Pipe) |  |  |  | Segment 3 (Existing 20" BWS Pipe) |  |  |  | Segment 4 (Newish 20" BWS Pipe) |  |  | 4000 | 8.92 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 4.0886 | 2.8393 | 4.0886 | 4.0886 | 0.76057 | 0.045066 | 0.33486 | 0.17132 | 0.037948 | 0.085075 | 7.4463 | 0.47708 | 1.3118 | 8.0464 | 20.09 | 10.06 | 29.4482 | 19.4182
hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | 4500 | 10.035 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 4.5997 | 3.1942 | 4.5997 | 4.5997 | 0.96259 | 0.057036 | 0.4238 | 0.21683 | 0.047187 | 0.10579 | 9.2591 | 0.59323 | 1.6603 | 10.0053 | 20.09 | 10.06 | 31.7556 | 21.7256
L = Length of pipe (ft) |  | 12 |  | L = Length of pipe (ft) |  | 65 |  | L = Length of pipe (ft) |  | 1375 | ft | L = Length of pipe (ft) | 150 | ft | 5000 | 11.15 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 5.1108 | 3.5492 | 5.1108 | 5.1108 | 1.1884 | 0.070415 | 0.52321 | 0.26769 | 0.057342 | 0.12855 | 11.2518 | 0.7209 | 2.0497 | 12.1586 | 20.09 | 10.06 | 34.2983 | 24.2683
D = Inner Diameter of pipe (in) |  | 20 |  | D = Inner Diameter of pipe (in) |  | 24 |  | D = Inner Diameter of pipe (in) |  | 20 | in | D = Inner Diameter of pipe (in) | 20 | in | 5500 | 12.265 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 5.6219 | 3.9041 | 5.6219 | 5.6219 | 1.4379 | 0.085202 | 0.63309 | 0.32391 | 0.068399 | 0.15334 | 13.4214 | 0.8599 | 2.4801 | 14.5031 | 20.09 | 10.06 | 37.0732 | 27.0432
C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 90 |  | C = HW coefficient (table above) | 120 |  | 6000 | 13.38 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 6.1329 | 4.259 | 6.1329 | 6.1329 | 1.7113 | 0.1014 | 0.75343 | 0.38547 | 0.080345 | 0.18012 | 15.7655 | 1.0101 | 2.9516 | 17.036 | 20.09 | 10.06 | 40.0776 | 30.0476
[15 empty] | 6500 | 14.495 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 6.644 | 4.6139 | 6.644 | 6.644 | 2.0084 | 0.119 | 0.88423 | 0.4524 | 0.093169 | 0.20887 | 18.2817 | 1.1713 | 3.464 | 19.7551 | 20.09 | 10.06 | 43.3091 | 33.2791
[15 empty] | 7000 | 15.61 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 7.1551 | 4.9688 | 7.1551 | 7.1551 | 2.3292 | 0.13801 | 1.0255 | 0.52467 | 0.10686 | 0.23956 | 20.9681 | 1.3434 | 4.0174 | 22.6579 | 20.09 | 10.06 | 46.7653 | 36.7353
[15 empty] | 7500 | 16.725 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 7.6662 | 5.3237 | 7.6662 | 7.6662 | 2.6739 | 0.15843 | 1.1772 | 0.6023 | 0.12141 | 0.27218 | 23.8227 | 1.5263 | 4.6118 | 25.7426 | 20.09 | 10.06 | 50.4444 | 40.4144
[15 empty] | 8000 | 17.84 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 8.1773 | 5.6786 | 8.1773 | 8.1773 | 3.0423 | 0.18026 | 1.3394 | 0.68529 | 0.1368 | 0.30669 | 26.8438 | 1.7199 | 5.2472 | 29.0072 | 20.09 | 10.06 | 54.3444 | 44.3144
[15 empty] | 8500 | 18.955 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 8.6883 | 6.0336 | 8.6883 | 8.6883 | 3.4344 | 0.2035 | 1.5121 | 0.77363 | 0.15304 | 0.34309 | 30.0298 | 1.924 | 5.9236 | 32.4499 | 20.09 | 10.06 | 58.4636 | 48.4336
MINOR LOSSES | K | qty |  | MINOR LOSSES | K | qty |  | MINOR LOSSES | K | qty |  | MINOR LOSSES | K | qty | 9000 | 20.07 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 9.1994 | 6.3885 | 9.1994 | 9.1994 | 3.8504 | 0.22815 | 1.6952 | 0.86732 | 0.17011 | 0.38136 | 33.3792 | 2.1386 | 6.641 | 36.0693 | 20.09 | 10.06 | 62.8003 | 52.7703
Entry Losses | 0.5 | 1 |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  | 9500 | 21.185 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 9.7105 | 6.7434 | 9.7105 | 9.7105 | 4.2901 | 0.2542 | 1.8888 | 0.96636 | 0.188 | 0.42148 | 36.8906 | 2.3636 | 7.3994 | 39.8637 | 20.09 | 10.06 | 67.3531 | 57.3231
Reducer |  |  |  | Reducer |  |  |  | Reducer |  |  |  | Reducer |  | 0 | 10000 | 22.3 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 10.2216 | 7.0983 | 10.2216 | 10.2216 | 4.7535 | 0.28166 | 2.0929 | 1.0708 | 0.20672 | 0.46343 | 40.5627 | 2.5988 | 8.1988 | 43.8317 | 20.09 | 10.06 | 72.1205 | 62.0905
Bellmouth | 0.05 | 1 |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  | 10500 | 23.415 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 10.7326 | 7.4532 | 10.7326 | 10.7326 | 5.2408 | 0.31053 | 2.3074 | 1.1805 | 0.22625 | 0.50721 | 44.3943 | 2.8443 | 9.0392 | 47.9721 | 20.09 | 10.06 | 77.1013 | 67.0713
Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  | 10800 | 24.084 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 11.0393 | 7.6662 | 11.0393 | 11.0393 | 5.5445 | 0.32853 | 2.4411 | 1.2489 | 0.23835 | 0.53435 | 46.7693 | 2.9965 | 9.5631 | 50.5385 | 20.09 | 10.06 | 80.1916 | 70.1616
Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  | 11000 | 24.53 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 11.2437 | 7.8081 | 11.2437 | 11.2437 | 5.7518 | 0.34081 | 2.5324 | 1.2956 | 0.24658 | 0.5528 | 48.3842 | 3.1 | 9.9206 | 52.2836 | 20.09 | 10.06 | 82.2941 | 72.2641
Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  | 11500 | 25.645 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 11.7548 | 8.1631 | 11.7548 | 11.7548 | 6.2866 | 0.3725 | 2.7678 | 1.4161 | 0.26771 | 0.60018 | 52.5313 | 3.3657 | 10.8429 | 56.7649 | 20.09 | 10.06 | 87.6978 | 77.6678
Exit Loss | 1 |  |  | Exit Loss | 1 |  |  | Exit Loss | 1 |  |  | Exit Loss | 1 | 0 | 12000 | 26.76 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 12.2659 | 8.518 | 12.2659 | 12.2659 | 6.8451 | 0.40559 | 3.0137 | 1.5419 | 0.28964 | 0.64934 | 56.8346 | 3.6414 | 11.8063 | 61.4149 | 20.09 | 10.06 | 93.3112 | 83.2812
90 deg Ell, std | 0.36 | 3 |  | 90 deg Ell, std | 0.36 | 1 |  | 90 deg Ell, std | 0.36 | 2 |  | 90 deg Ell, std | 0.36 | 1 | 12500 | 27.875 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 12.777 | 8.8729 | 12.777 | 12.777 | 7.4274 | 0.4401 | 3.2701 | 1.6731 | 0.31237 | 0.70028 | 61.293 | 3.927 | 12.8106 | 66.2327 | 20.09 | 10.06 | 99.1333 | 89.1033
91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  | 13000 | 28.99 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 13.288 | 9.2278 | 13.288 | 13.288 | 8.0335 | 0.47601 | 3.5369 | 1.8096 | 0.33587 | 0.75298 | 65.9056 | 4.2225 | 13.856 | 71.217 | 20.09 | 10.06 | 105.163 | 95.133
45 deg Ell, std | 0.19 |  |  | 45 deg Ell, std | 0.19 | 0 |  | 45 deg Ell, std | 0.19 | 3 |  | 45 deg Ell, std | 0.19 |  | 13500 | 30.105 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 13.7991 | 9.5827 | 13.7991 | 13.7991 | 8.6633 | 0.51333 | 3.8142 | 1.9515 | 0.36016 | 0.80743 | 70.6716 | 4.5279 | 14.9423 | 76.3671 | 20.09 | 10.06 | 111.3994 | 101.3694
45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  | 14000 | 31.22 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 14.3102 | 9.9376 | 14.3102 | 14.3102 | 9.3169 | 0.55206 | 4.102 | 2.0987 | 0.38523 | 0.86363 | 75.59 | 4.843 | 16.0697 | 81.6818 | 20.09 | 10.06 | 117.8415 | 107.8115
Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  | 14500 | 32.335 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 14.8213 | 10.2926 | 14.8213 | 14.8213 | 9.9943 | 0.59219 | 4.4002 | 2.2513 | 0.41107 | 0.92155 | 80.66 | 5.1679 | 17.238 | 87.1604 | 20.09 | 10.06 | 124.4884 | 114.4584
Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 | 15000 | 33.45 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 15.3324 | 10.6475 | 15.3324 | 15.3324 | 10.6955 | 0.63374 | 4.7089 | 2.4092 | 0.43767 | 0.9812 | 85.8808 | 5.5023 | 18.4473 | 92.802 | 20.09 | 10.06 | 131.3394 | 121.3094
Coupling | 0.04 |  |  | Coupling | 0.04 |  |  | Coupling | 0.04 |  |  | Coupling | 0.04 |  | 15500 | 34.565 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 15.8434 | 11.0024 | 15.8434 | 15.8434 | 11.4204 | 0.67669 | 5.0281 | 2.5725 | 0.46504 | 1.0426 | 91.2517 | 5.8465 | 19.6976 | 98.6058 | 20.09 | 10.06 | 138.3934 | 128.3634
Union | 0.04 |  |  | Union | 0.04 |  |  | Union | 0.04 |  |  | Union | 0.04 |  | 16000 | 35.68 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 16.3545 | 11.3573 | 16.3545 | 16.3545 | 12.1691 | 0.72105 | 5.3577 | 2.7412 | 0.49318 | 1.1056 | 96.7719 | 6.2001 | 20.989 | 104.5708 | 20.09 | 10.06 | 145.6498 | 135.6198
Butterfly Valve, Open | 0.3 | 2 |  | Butterfly Valve, Open | 0.3 |  |  | Butterfly Valve, Open | 0.3 |  |  | Butterfly Valve, Open | 0.3 | 1 | 16500 | 36.795 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 16.8656 | 11.7122 | 16.8656 | 16.8656 | 12.9415 | 0.76682 | 5.6978 | 2.9152 | 0.52207 | 1.1704 | 102.4407 | 6.5633 | 22.3213 | 110.6965 | 20.09 | 10.06 | 153.1078 | 143.0778
Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  | 17000 | 37.91 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 17.3767 | 12.0671 | 17.3767 | 17.3767 | 13.7377 | 0.814 | 6.0483 | 3.0945 | 0.55171 | 1.2369 | 108.2574 | 6.936 | 23.6946 | 116.982 | 20.09 | 10.06 | 160.7666 | 150.7366
Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  | 17500 | 39.025 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 17.8877 | 12.422 | 17.8877 | 17.8877 | 14.5577 | 0.86259 | 6.4094 | 3.2792 | 0.5821 | 1.305 | 114.2214 | 7.3181 | 25.1089 | 123.4267 | 20.09 | 10.06 | 168.6255 | 158.5955
Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  | 18000 | 40.14 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 18.3988 | 12.777 | 18.3988 | 18.3988 | 15.4015 | 0.91258 | 6.7808 | 3.4693 | 0.61325 | 1.3748 | 120.3321 | 7.7096 | 26.5642 | 130.0298 | 20.09 | 10.06 | 176.6839 | 166.6539
Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  | 18500 | 41.255 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 18.9099 | 13.1319 | 18.9099 | 18.9099 | 16.269 | 0.96398 | 7.1628 | 3.6647 | 0.64513 | 1.4463 | 126.5887 | 8.1105 | 28.0604 | 136.7906 | 20.09 | 10.06 | 184.9411 | 174.9111
Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  | 19000 | 42.37 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 19.421 | 13.4868 | 19.421 | 19.421 | 17.1603 | 1.0168 | 7.5552 | 3.8655 | 0.67776 | 1.5194 | 132.9908 | 8.5207 | 29.5977 | 143.7086 | 20.09 | 10.06 | 193.3963 | 183.3663
Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  | 19500 | 43.485 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 19.9321 | 13.8417 | 19.9321 | 19.9321 | 18.0753 | 1.071 | 7.9581 | 4.0716 | 0.71112 | 1.5942 | 139.5376 | 8.9401 | 31.176 | 150.7831 | 20.09 | 10.06 | 202.0491 | 192.0191
Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  | 20000 | 44.6 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 20.4431 | 14.1966 | 20.4431 | 20.4431 | 19.0141 | 1.1266 | 8.3714 | 4.283 | 0.74522 | 1.6707 | 146.2288 | 9.3688 | 32.7952 | 158.0135 | 20.09 | 10.06 | 210.8987 | 200.8687
Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  | 20500 | 45.715 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 20.9542 | 14.5515 | 20.9542 | 20.9542 | 19.9767 | 1.1837 | 8.7952 | 4.4999 | 0.78005 | 1.7488 | 153.0636 | 9.8067 | 34.4555 | 165.3991 | 20.09 | 10.06 | 219.9447 | 209.9147
Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  | 21000 | 46.83 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 21.4653 | 14.9065 | 21.4653 | 21.4653 | 20.9631 | 1.2421 | 9.2295 | 4.7221 | 0.81562 | 1.8285 | 160.0416 | 10.2538 | 36.1568 | 172.9395 | 20.09 | 10.06 | 229.1863 | 219.1563
Metal swing check valve | 1.2 | 1 |  | Metal swing check valve | 1.2 |  |  | Metal swing check valve | 1.2 |  |  | Metal swing check valve | 1.2 |  | 21500 | 47.945 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 21.9764 | 15.2614 | 21.9764 | 21.9764 | 21.9732 | 1.302 | 9.6742 | 4.9496 | 0.85191 | 1.9099 | 167.1623 | 10.71 | 37.899 | 180.6341 | 20.09 | 10.06 | 238.6231 | 228.5931
Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  | 22000 | 49.06 | 2.1817 | 3.1416 | 2.1817 | 2.1817 | 22.4874 | 15.6163 | 22.4874 | 22.4874 | 23.0071 | 1.3632 | 10.1294 | 5.1825 | 0.88892 | 1.9928 | 174.4252 | 11.1753 | 39.6822 | 188.4823 | 20.09 | 10.06 | 248.2546 | 238.2246
Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04
TOTAL K IN APP | 2.93 |  |  | TOTAL K IN APP | 0.36 |  |  | TOTAL K IN APP | 1.29 |  |  | TOTAL K IN APP | 0.66
Note on B27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on F27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on J27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on N27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4

## BWR Sys Curve - Rep w 24" IPS
SYSTEM CURVE
| Min. Wet Well WSE | 5176.23 | Current pump 1 on depth |  |  |  | Existing Set Points in Wetwell
| Max. Wet Well EL | 5180.01 | OVF |  |  |  | Low | 5 | ft | [10 empty] | Describe What Seg 1 and 2 include, need separate segments for VT Pump Column and Discharge Heard
| Min Exit EL | 5190.07 | Best guess, to be confirmed with 2004 B&C Drawings |  |  |  | High Alarm | 10 | ft | [10 empty] | We cannot stamp an 11 fps velocity.
| Max Exit El | 5196.32 |  |  |  |  | High High | 10.2 | ft
STATIC HEAD | [17 empty] | Flow |  | Seg 1 Area | Seg 2 Area | Seg 3 Area | Seg 4 Area | Seg 5 Area | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Seg 4 Velocity | Seg 5 Velocity | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Seg 4 h_minor | Seg 5 h_minor | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | Seg 4 h_friction | Seg 5 h_friction | h_minor total | h_friction total | h_delta_max | h_delta_min | TDH Max | TDH Min
Max. Total Static Head |  | 20.09 | [15 empty] | gpm | cfs | sf | sf | sf | sf | sf | fps | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft
Min Total Static Head |  | 10.06 | [15 empty] | 0 | 0 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.09 | 10.06 | 20.09 | 10.06
[18 empty] | 500 | 1.115 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 0.51108 | 0.51108 | 0.46325 | 0.51108 | 0.51108 | 0.0002028 | 0.014682 | 0.0025326 | 0.0012168 | 0.0069762 | 0.00080998 | 0.0054309 | 0.054326 | 0.010183 | 0.0033943 | 0.025611 | 0.074145 | 20.09 | 10.06 | 20.1898 | 10.1598
FRICTION LOSS | [17 empty] | 1000 | 2.23 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 1.0222 | 1.0222 | 0.92651 | 1.0222 | 1.0222 | 0.00081118 | 0.05873 | 0.01013 | 0.0048671 | 0.027905 | 0.00292 | 0.019578 | 0.19585 | 0.03671 | 0.012237 | 0.10244 | 0.26729 | 20.09 | 10.06 | 20.4597 | 10.4297
Hazen Williams Coefficients |  | C_water | C_wastewater | [14 empty] | 1500 | 3.345 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 1.5332 | 1.5332 | 1.3898 | 1.5332 | 1.5332 | 0.0018252 | 0.13214 | 0.022793 | 0.010951 | 0.062786 | 0.0061823 | 0.041452 | 0.41465 | 0.077723 | 0.025908 | 0.2305 | 0.56592 | 20.09 | 10.06 | 20.8864 | 10.8564
DI |  | 80-120 | 80-110 | [14 empty] | 2000 | 4.46 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 2.0443 | 2.0443 | 1.853 | 2.0443 | 2.0443 | 0.0032447 | 0.23492 | 0.040522 | 0.019468 | 0.11162 | 0.010527 | 0.07058 | 0.70603 | 0.13234 | 0.044113 | 0.40977 | 0.96359 | 20.09 | 10.06 | 21.4634 | 11.4334
Steel |  | 110-130 | 110-130 | [14 empty] | 2500 | 5.575 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 2.5554 | 2.5554 | 2.3163 | 2.5554 | 2.5554 | 0.0050699 | 0.36706 | 0.063315 | 0.030419 | 0.1744 | 0.015906 | 0.10665 | 1.0669 | 0.19997 | 0.066657 | 0.64027 | 1.456 | 20.09 | 10.06 | 22.1863 | 12.1563
PVC |  | 135-150 | 130-145 | [14 empty] | 3000 | 6.69 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 3.0665 | 3.0665 | 2.7795 | 3.0665 | 3.0665 | 0.0073007 | 0.52857 | 0.091174 | 0.043804 | 0.25114 | 0.022287 | 0.14943 | 1.4948 | 0.28019 | 0.093397 | 0.92199 | 2.0401 | 20.09 | 10.06 | 23.0521 | 13.0221
[18 empty] | 3500 | 7.805 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 3.5775 | 3.5775 | 3.2428 | 3.5775 | 3.5775 | 0.009937 | 0.71944 | 0.1241 | 0.059622 | 0.34183 | 0.029642 | 0.19875 | 1.9881 | 0.37265 | 0.12422 | 1.2549 | 2.7134 | 20.09 | 10.06 | 24.0583 | 14.0283
Segment 1 (Pump Suction Pipe) |  |  |  | Segment 2 (Pump Discharge Pipe) |  |  |  | Segment 3 (New 24" BWS Pipe) |  |  |  | Segment 4 (Newish 20" BWS Pipe) |  |  | Segment 5 (New Tie-in to EQ) |  |  | 4000 | 8.92 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 4.0886 | 4.0886 | 3.706 | 4.0886 | 4.0886 | 0.012979 | 0.93967 | 0.16209 | 0.077874 | 0.44648 | 0.037948 | 0.25444 | 2.5452 | 0.47708 | 0.15903 | 1.6391 | 3.4737 | 20.09 | 10.06 | 25.2028 | 15.1728
hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | 4500 | 10.035 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 4.5997 | 4.5997 | 4.1693 | 4.5997 | 4.5997 | 0.016426 | 1.1893 | 0.20514 | 0.098559 | 0.56507 | 0.047187 | 0.31639 | 3.1649 | 0.59323 | 0.19774 | 2.0745 | 4.3194 | 20.09 | 10.06 | 26.4839 | 16.4539
L = Length of pipe (ft) |  | 12 |  | L = Length of pipe (ft) |  | 80 |  | L = Length of pipe (ft) |  | 1352 | ft | L = Length of pipe (ft) | 150 | ft | L = Length of pipe (ft) | 50 | ft | 5000 | 11.15 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 5.1108 | 5.1108 | 4.6325 | 5.1108 | 5.1108 | 0.02028 | 1.4682 | 0.25326 | 0.12168 | 0.69762 | 0.057342 | 0.38448 | 3.846 | 0.7209 | 0.2403 | 2.5611 | 5.249 | 20.09 | 10.06 | 27.9001 | 17.8701
D = Inner Diameter of pipe (in) |  | 20 |  | D = Inner Diameter of pipe (in) |  | 20 |  | D = Inner Diameter of pipe (in) |  | 21.007 | in | D = Inner Diameter of pipe (in) | 20 | in | D = Inner Diameter of pipe (in) | 20 | in | 5500 | 12.265 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 5.6219 | 5.6219 | 5.0958 | 5.6219 | 5.6219 | 0.024538 | 1.7766 | 0.30644 | 0.14723 | 0.84412 | 0.068399 | 0.45862 | 4.5876 | 0.8599 | 0.28663 | 3.0989 | 6.2612 | 20.09 | 10.06 | 29.4501 | 19.4201
C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 140 |  | C = HW coefficient (table above) | 120 |  | C = HW coefficient (table above) | 120 |  | 6000 | 13.38 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 6.1329 | 6.1329 | 5.5591 | 6.1329 | 6.1329 | 0.029203 | 2.1143 | 0.36469 | 0.17522 | 1.0046 | 0.080345 | 0.53871 | 5.3888 | 1.0101 | 0.3367 | 3.688 | 7.3547 | 20.09 | 10.06 | 31.1326 | 21.1026
[18 empty] | 6500 | 14.495 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 6.644 | 6.644 | 6.0223 | 6.644 | 6.644 | 0.034273 | 2.4813 | 0.42801 | 0.20564 | 1.179 | 0.093169 | 0.62469 | 6.2489 | 1.1713 | 0.39043 | 4.3282 | 8.5285 | 20.09 | 10.06 | 32.9468 | 22.9168
[18 empty] | 7000 | 15.61 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 7.1551 | 7.1551 | 6.4856 | 7.1551 | 7.1551 | 0.039748 | 2.8778 | 0.49639 | 0.23849 | 1.3673 | 0.10686 | 0.71649 | 7.1672 | 1.3434 | 0.44781 | 5.0197 | 9.7817 | 20.09 | 10.06 | 34.8914 | 24.8614
[18 empty] | 7500 | 16.725 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 7.6662 | 7.6662 | 6.9488 | 7.6662 | 7.6662 | 0.045629 | 3.3035 | 0.56983 | 0.27377 | 1.5696 | 0.12141 | 0.81403 | 8.1429 | 1.5263 | 0.50877 | 5.7624 | 11.1134 | 20.09 | 10.06 | 36.9659 | 26.9359
[18 empty] | 8000 | 17.84 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 8.1773 | 8.1773 | 7.4121 | 8.1773 | 8.1773 | 0.051916 | 3.7587 | 0.64835 | 0.31149 | 1.7859 | 0.1368 | 0.91726 | 9.1756 | 1.7199 | 0.57329 | 6.5564 | 12.5228 | 20.09 | 10.06 | 39.1691 | 29.1391
[18 empty] | 8500 | 18.955 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 8.6883 | 8.6883 | 7.8753 | 8.6883 | 8.6883 | 0.058608 | 4.2432 | 0.73192 | 0.35165 | 2.0161 | 0.15304 | 1.0261 | 10.2646 | 1.924 | 0.64133 | 7.4015 | 14.0091 | 20.09 | 10.06 | 41.5006 | 31.4706
MINOR LOSSES | K | qty |  | MINOR LOSSES | K | qty |  | MINOR LOSSES | K |  |  | MINOR LOSSES | K |  | MINOR LOSSES | K |  | 9000 | 20.07 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 9.1994 | 9.1994 | 8.3386 | 9.1994 | 9.1994 | 0.065706 | 4.7571 | 0.82056 | 0.39424 | 2.2603 | 0.17011 | 1.1406 | 11.4095 | 2.1386 | 0.71286 | 8.2979 | 15.5716 | 20.09 | 10.06 | 43.9595 | 33.9295
Entry Losses | 0.5 | 1 |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  | Entry Losses | 0.5 | qty | 9500 | 21.185 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 9.7105 | 9.7105 | 8.8018 | 9.7105 | 9.7105 | 0.073209 | 5.3004 | 0.91427 | 0.43926 | 2.5184 | 0.188 | 1.2606 | 12.6097 | 2.3636 | 0.78786 | 9.2455 | 17.2097 | 20.09 | 10.06 | 46.5452 | 36.5152
Reducer |  |  |  | Reducer |  |  |  | Reducer |  |  |  | Reducer |  | 1 | Reducer |  | 0 | 10275 | 22.9133 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 10.5027 | 10.5027 | 9.5199 | 10.5027 | 10.5027 | 0.085641 | 6.2004 | 1.0695 | 0.51385 | 2.9461 | 0.21736 | 1.4574 | 14.5785 | 2.7326 | 0.91087 | 10.8155 | 19.8967 | 20.09 | 10.06 | 50.8022 | 40.7722
Bellmouth | 0.05 | 1 |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  | Bellmouth | 0.05 |  | 10500 | 23.415 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 10.7326 | 10.7326 | 9.7283 | 10.7326 | 10.7326 | 0.089433 | 6.4749 | 1.1169 | 0.5366 | 3.0765 | 0.22625 | 1.517 | 15.1746 | 2.8443 | 0.94811 | 11.2943 | 20.7102 | 20.09 | 10.06 | 52.0946 | 42.0646
Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  | Rounded | 0.25 |  | 10800 | 24.084 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 11.0393 | 11.0393 | 10.0063 | 11.0393 | 11.0393 | 0.094616 | 6.8502 | 1.1816 | 0.5677 | 3.2548 | 0.23835 | 1.5981 | 15.9864 | 2.9965 | 0.99883 | 11.949 | 21.8182 | 20.09 | 10.06 | 53.8571 | 43.8271
Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  | Sharp Edged | 0.5 |  | 11000 | 24.53 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 11.2437 | 11.2437 | 10.1916 | 11.2437 | 11.2437 | 0.098153 | 7.1063 | 1.2258 | 0.58892 | 3.3765 | 0.24658 | 1.6533 | 16.5384 | 3.1 | 1.0333 | 12.3956 | 22.5715 | 20.09 | 10.06 | 55.0571 | 45.0271
Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  | Projecting | 0.8 |  | 11500 | 25.645 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 11.7548 | 11.7548 | 10.6548 | 11.7548 | 11.7548 | 0.10728 | 7.767 | 1.3397 | 0.64367 | 3.6904 | 0.26771 | 1.795 | 17.9559 | 3.3657 | 1.1219 | 13.5481 | 24.5062 | 20.09 | 10.06 | 58.1443 | 48.1143
Exit Loss | 1 |  |  | Exit Loss | 1 |  |  | Exit Loss | 1 |  |  | Exit Loss | 1 | 0 | Exit Loss | 1 | 1 | 12000 | 26.76 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 12.2659 | 12.2659 | 11.1181 | 12.2659 | 12.2659 | 0.11681 | 8.4571 | 1.4588 | 0.70086 | 4.0183 | 0.28964 | 1.9421 | 19.4268 | 3.6414 | 1.2138 | 14.7518 | 26.5137 | 20.09 | 10.06 | 61.3555 | 51.3255
90 deg Ell, std | 0.36 | 0 |  | 90 deg Ell, std | 0.36 | 4 |  | 90 deg Ell, std | 0.36 | 0 |  | 90 deg Ell, std | 0.36 |  | 90 deg Ell, std | 0.36 |  | 12500 | 27.875 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 12.777 | 12.777 | 11.5814 | 12.777 | 12.777 | 0.12675 | 9.1765 | 1.5829 | 0.76048 | 4.3601 | 0.31237 | 2.0944 | 20.9508 | 3.927 | 1.309 | 16.0067 | 28.5936 | 20.09 | 10.06 | 64.6903 | 54.6603
91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  | 91 deg Ell, long radius | 0.19 |  | 13000 | 28.99 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 13.288 | 13.288 | 12.0446 | 13.288 | 13.288 | 0.13709 | 9.9253 | 1.712 | 0.82254 | 4.7159 | 0.33587 | 2.252 | 22.5274 | 4.2225 | 1.4075 | 17.3129 | 30.7454 | 20.09 | 10.06 | 68.1483 | 58.1183
45 deg Ell, std | 0.19 |  |  | 45 deg Ell, std | 0.19 | 2 |  | 45 deg Ell, std | 0.19 | 4 |  | 45 deg Ell, std | 0.19 |  | 45 deg Ell, std | 0.19 |  | 13500 | 30.105 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 13.7991 | 13.7991 | 12.5079 | 13.7991 | 13.7991 | 0.14784 | 10.7035 | 1.8463 | 0.88703 | 5.0856 | 0.36016 | 2.4149 | 24.1565 | 4.5279 | 1.5093 | 18.6703 | 32.9687 | 20.09 | 10.06 | 71.729 | 61.699
45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  | 45 deg Ell, long radius | 0.1 |  | 14000 | 31.22 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 14.3102 | 14.3102 | 12.9711 | 14.3102 | 14.3102 | 0.15899 | 11.511 | 1.9856 | 0.95395 | 5.4693 | 0.38523 | 2.5829 | 25.8377 | 4.843 | 1.6143 | 20.0788 | 35.2632 | 20.09 | 10.06 | 75.432 | 65.402
Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  | Tee, line flow | 0.24 |  | 14500 | 32.335 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 14.8213 | 14.8213 | 13.4344 | 14.8213 | 14.8213 | 0.17055 | 12.3479 | 2.1299 | 1.0233 | 5.867 | 0.41107 | 2.7562 | 27.5707 | 5.1679 | 1.7226 | 21.5387 | 37.6284 | 20.09 | 10.06 | 79.257 | 69.227
Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 | Tee, branch flow | 0.72 | 1 | 15000 | 33.45 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 15.3324 | 15.3324 | 13.8976 | 15.3324 | 15.3324 | 0.18252 | 13.2142 | 2.2793 | 1.0951 | 6.2786 | 0.43767 | 2.9346 | 29.3552 | 5.5023 | 1.8341 | 23.0497 | 40.0639 | 20.09 | 10.06 | 83.2036 | 73.1736
Coupling | 0.04 |  |  | Coupling | 0.04 |  |  | Coupling | 0.04 |  |  | Coupling | 0.04 |  | Coupling | 0.04 |  | 15500 | 34.565 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 15.8434 | 15.8434 | 14.3609 | 15.8434 | 15.8434 | 0.19489 | 14.1098 | 2.4338 | 1.1693 | 6.7041 | 0.46504 | 3.1181 | 31.191 | 5.8465 | 1.9488 | 24.6119 | 42.5695 | 20.09 | 10.06 | 87.2714 | 77.2414
Union | 0.04 |  |  | Union | 0.04 |  |  | Union | 0.04 |  |  | Union | 0.04 |  | Union | 0.04 |  | 16000 | 35.68 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 16.3545 | 16.3545 | 14.8241 | 16.3545 | 16.3545 | 0.20766 | 15.0348 | 2.5934 | 1.246 | 7.1436 | 0.49318 | 3.3067 | 33.0779 | 6.2001 | 2.0667 | 26.2254 | 45.1447 | 20.09 | 10.06 | 91.4601 | 81.4301
Butterfly Valve, Open | 0.3 | 0 |  | Butterfly Valve, Open | 0.3 | 2 |  | Butterfly Valve, Open | 0.3 |  |  | Butterfly Valve, Open | 0.3 | 1 | Butterfly Valve, Open | 0.3 | 0 | 16500 | 36.795 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 16.8656 | 16.8656 | 15.2874 | 16.8656 | 16.8656 | 0.22084 | 15.9892 | 2.758 | 1.3251 | 7.5971 | 0.52207 | 3.5004 | 35.0156 | 6.5633 | 2.1878 | 27.8901 | 47.7892 | 20.09 | 10.06 | 95.7694 | 85.7394
Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  | Gate Valve, open | 0.1 |  | 17000 | 37.91 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 17.3767 | 17.3767 | 15.7506 | 17.3767 | 17.3767 | 0.23443 | 16.9729 | 2.9277 | 1.4066 | 8.0645 | 0.55171 | 3.6992 | 37.0038 | 6.936 | 2.312 | 29.606 | 50.5028 | 20.09 | 10.06 | 100.1988 | 90.1688
Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  | Gate Valve, 3/4 open | 0.9 |  | 17500 | 39.025 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 17.8877 | 17.8877 | 16.2139 | 17.8877 | 17.8877 | 0.24842 | 17.986 | 3.1024 | 1.4905 | 8.5458 | 0.5821 | 3.903 | 39.0424 | 7.3181 | 2.4394 | 31.3732 | 53.285 | 20.09 | 10.06 | 104.7482 | 94.7182
Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  | Gate Valve, 1/2 open | 4.5 |  | 18000 | 40.14 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 18.3988 | 18.3988 | 16.6772 | 18.3988 | 18.3988 | 0.26282 | 19.0284 | 3.2822 | 1.5769 | 9.0411 | 0.61325 | 4.1118 | 41.1311 | 7.7096 | 2.5699 | 33.1916 | 56.1357 | 20.09 | 10.06 | 109.4172 | 99.3872
Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  | Gate Valve, 1/4 open | 24 |  | 18500 | 41.255 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 18.9099 | 18.9099 | 17.1404 | 18.9099 | 18.9099 | 0.27763 | 20.1002 | 3.4671 | 1.6658 | 9.5504 | 0.64513 | 4.3256 | 43.2697 | 8.1105 | 2.7035 | 35.0611 | 59.0544 | 20.09 | 10.06 | 114.2056 | 104.1756
Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  | Cross, line flow | 0.5 |  | 19000 | 42.37 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 19.421 | 19.421 | 17.6037 | 19.421 | 19.421 | 0.29284 | 21.2014 | 3.6571 | 1.757 | 10.0736 | 0.67776 | 4.5444 | 45.458 | 8.5207 | 2.8402 | 36.982 | 62.041 | 20.09 | 10.06 | 119.113 | 109.083
Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  | Cross, branch flow | 0.75 |  | 19500 | 43.485 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 19.9321 | 19.9321 | 18.0669 | 19.9321 | 19.9321 | 0.30845 | 22.332 | 3.8521 | 1.8507 | 10.6108 | 0.71112 | 4.7681 | 47.6958 | 8.9401 | 2.98 | 38.954 | 65.0952 | 20.09 | 10.06 | 124.1391 | 114.1091
Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  | Wye | 0.5 |  | 20000 | 44.6 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 20.4431 | 20.4431 | 18.5302 | 20.4431 | 20.4431 | 0.32447 | 23.4919 | 4.0522 | 1.9468 | 11.1619 | 0.74522 | 4.9967 | 49.9829 | 9.3688 | 3.1229 | 40.9772 | 68.2166 | 20.09 | 10.06 | 129.2838 | 119.2538
Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  | Ball Check Valve | 0.66 |  | 20500 | 45.715 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 20.9542 | 20.9542 | 18.9934 | 20.9542 | 20.9542 | 0.3409 | 24.6811 | 4.2573 | 2.0454 | 11.727 | 0.78005 | 5.2303 | 52.3192 | 9.8067 | 3.2689 | 43.0517 | 71.4051 | 20.09 | 10.06 | 134.5468 | 124.5168
Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  | Rubber swingcheck valve | 1.2 |  | 21000 | 46.83 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 21.4653 | 21.4653 | 19.4567 | 21.4653 | 21.4653 | 0.35773 | 25.8998 | 4.4675 | 2.1464 | 12.306 | 0.81562 | 5.4687 | 54.7044 | 10.2538 | 3.4179 | 45.1774 | 74.6604 | 20.09 | 10.06 | 139.9278 | 129.8978
Metal swing check valve | 1.2 | 0 |  | Metal swing check valve | 1.2 | 1 |  | Metal swing check valve | 1.2 |  |  | Metal swing check valve | 1.2 |  | Metal swing check valve | 1.2 |  | 21500 | 47.945 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 21.9764 | 21.9764 | 19.9199 | 21.9764 | 21.9764 | 0.37497 | 27.1478 | 4.6828 | 2.2498 | 12.899 | 0.85191 | 5.712 | 57.1383 | 10.71 | 3.57 | 47.3543 | 77.9823 | 20.09 | 10.06 | 145.4266 | 135.3966
Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  | Gate Valve | 0.1 |  | 22000 | 49.06 | 2.1817 | 2.1817 | 2.4069 | 2.1817 | 2.1817 | 22.4874 | 22.4874 | 20.3832 | 22.4874 | 22.4874 | 0.39261 | 28.4252 | 4.9031 | 2.3557 | 13.5059 | 0.88892 | 5.9602 | 59.6209 | 11.1753 | 3.7251 | 49.5825 | 81.3704 | 20.09 | 10.06 | 151.0429 | 141.0129
Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  | Ball Valve | 0.04
TOTAL K IN APP | 0.05 |  |  | TOTAL K IN APP | 3.62 |  |  | TOTAL K IN APP | 0.76 |  |  | TOTAL K IN APP | 0.3 |  | TOTAL K IN APP | 1.72
Note on B27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on F27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on J27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on N27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on R27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4

## BWR Sys Curve - Rep w 24" DIPS
SYSTEM CURVE
| Min. Wet Well WSE | 5176.23 | Current pump 1 on depth |  |  |  | Existing Set Points in Wetwell
| Max. Wet Well EL | 5180.01 | OVF |  |  |  | Low | 5 | ft | [10 empty] | Describe What Seg 1 and 2 include, need separate segments for VT Pump Column and Discharge Heard
| Min Exit EL | 5190.07 | Best guess, to be confirmed with 2004 B&C Drawings |  |  |  | High Alarm | 10 | ft | [10 empty] | We cannot stamp an 11 fps velocity.
| Max Exit El | 5196.32 |  |  |  |  | High High | 10.2 | ft
STATIC HEAD | [17 empty] | Flow |  | Seg 1 Area | Seg 2 Area | Seg 3 Area | Seg 4 Area | Seg 5 Area | Seg 1 Velocity | Seg 2 Velocity | Seg 3 Velocity | Seg 4 Velocity | Seg 5 Velocity | Seg 1 h_minor | Seg 2 h_minor | Seg 3 h_minor | Seg 4 h_minor | Seg 5 h_minor | Seg 1 h_friction | Seg 2 h_friction | Seg 3 h_friction | Seg 4 h_friction | Seg 5 h_friction | h_minor total | h_friction total | h_delta_max | h_delta_min | TDH Max | TDH Min
Max. Total Static Head |  | 20.09 | [15 empty] | gpm | cfs | sf | sf | sf | sf | sf | fps | fps | fps | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft | ft
Min Total Static Head |  | 10.06 | [15 empty] | 0 | 0 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.09 | 10.06 | 20.09 | 10.06
[18 empty] | 500 | 1.115 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 0.51108 | 0.51108 | 0.33239 | 0.51108 | 0.51108 | 0.0002028 | 0.014682 | 0.0013038 | 0.0012168 | 0.0069762 | 0.00080998 | 0.0044126 | 0.024207 | 0.010183 | 0.0033943 | 0.024382 | 0.043007 | 20.09 | 10.06 | 20.1574 | 10.1274
FRICTION LOSS |  | C_water | C_wastewater | [14 empty] | 1000 | 2.23 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 1.0222 | 1.0222 | 0.66477 | 1.0222 | 1.0222 | 0.00081118 | 0.05873 | 0.0052153 | 0.0048671 | 0.027905 | 0.00292 | 0.015907 | 0.087267 | 0.03671 | 0.012237 | 0.097528 | 0.15504 | 20.09 | 10.06 | 20.3426 | 10.3126
Hazen Williams Coefficients |  | 80-120 | 80-110 | [14 empty] | 1500 | 3.345 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 1.5332 | 1.5332 | 0.99716 | 1.5332 | 1.5332 | 0.0018252 | 0.13214 | 0.011734 | 0.010951 | 0.062786 | 0.0061823 | 0.03368 | 0.18476 | 0.077723 | 0.025908 | 0.21944 | 0.32826 | 20.09 | 10.06 | 20.6377 | 10.6077
DI |  | 110-130 | 110-130 | [14 empty] | 2000 | 4.46 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 2.0443 | 2.0443 | 1.3295 | 2.0443 | 2.0443 | 0.0032447 | 0.23492 | 0.020861 | 0.019468 | 0.11162 | 0.010527 | 0.057346 | 0.3146 | 0.13234 | 0.044113 | 0.39011 | 0.55892 | 20.09 | 10.06 | 21.039 | 11.009
Steel |  | 135-150 | 130-145 | [14 empty] | 2500 | 5.575 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 2.5554 | 2.5554 | 1.6619 | 2.5554 | 2.5554 | 0.0050699 | 0.36706 | 0.032595 | 0.030419 | 0.1744 | 0.015906 | 0.086654 | 0.47538 | 0.19997 | 0.066657 | 0.60955 | 0.84457 | 20.09 | 10.06 | 21.5441 | 11.5141
PVC | [17 empty] | 3000 | 6.69 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 3.0665 | 3.0665 | 1.9943 | 3.0665 | 3.0665 | 0.0073007 | 0.52857 | 0.046937 | 0.043804 | 0.25114 | 0.022287 | 0.12142 | 0.66608 | 0.28019 | 0.093397 | 0.87775 | 1.1834 | 20.09 | 10.06 | 22.1511 | 12.1211
[18 empty] | 3500 | 7.805 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 3.5775 | 3.5775 | 2.3267 | 3.5775 | 3.5775 | 0.009937 | 0.71944 | 0.063887 | 0.059622 | 0.34183 | 0.029642 | 0.16148 | 0.88588 | 0.37265 | 0.12422 | 1.1947 | 1.5739 | 20.09 | 10.06 | 22.8586 | 12.8286
Segment 1 (Pump Suction Pipe) |  |  |  | Segment 2 (Pump Discharge Pipe) |  |  |  | Segment 3 (New 24" BWS Pipe) |  |  |  | Segment 4 (Existing 20" BWS Pipe) |  |  | Segment 5 (New Tie-in to EQ) |  |  | 4000 | 8.92 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 4.0886 | 4.0886 | 2.6591 | 4.0886 | 4.0886 | 0.012979 | 0.93967 | 0.083444 | 0.077874 | 0.44648 | 0.037948 | 0.20673 | 1.1341 | 0.47708 | 0.15903 | 1.5604 | 2.0149 | 20.09 | 10.06 | 23.6654 | 13.6354
hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  | 4500 | 10.035 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 4.5997 | 4.5997 | 2.9915 | 4.5997 | 4.5997 | 0.016426 | 1.1893 | 0.10561 | 0.098559 | 0.56507 | 0.047187 | 0.25707 | 1.4102 | 0.59323 | 0.19774 | 1.9749 | 2.5055 | 20.09 | 10.06 | 24.5704 | 14.5404
L = Length of pipe (ft) |  | 12 |  | L = Length of pipe (ft) |  | 65 |  | L = Length of pipe (ft) |  | 1352 | ft | L = Length of pipe (ft) | 150 | ft | L = Length of pipe (ft) | 50 | ft | 5000 | 11.15 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 5.1108 | 5.1108 | 3.3239 | 5.1108 | 5.1108 | 0.02028 | 1.4682 | 0.13038 | 0.12168 | 0.69762 | 0.057342 | 0.31239 | 1.7137 | 0.7209 | 0.2403 | 2.4382 | 3.0447 | 20.09 | 10.06 | 25.5729 | 15.5429
D = Inner Diameter of pipe (in) |  | 20 |  | D = Inner Diameter of pipe (in) |  | 20 |  | D = Inner Diameter of pipe (in) |  | 24.8 | in | D = Inner Diameter of pipe (in) | 20 | in | D = Inner Diameter of pipe (in) | 20 | in | 5500 | 12.265 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 5.6219 | 5.6219 | 3.6563 | 5.6219 | 5.6219 | 0.024538 | 1.7766 | 0.15776 | 0.14723 | 0.84412 | 0.068399 | 0.37263 | 2.0442 | 0.8599 | 0.28663 | 2.9502 | 3.6317 | 20.09 | 10.06 | 26.672 | 16.642
C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 140 |  | C = HW coefficient (table above) | 120 |  | C = HW coefficient (table above) | 120 |  | 6000 | 13.38 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 6.1329 | 6.1329 | 3.9886 | 6.1329 | 6.1329 | 0.029203 | 2.1143 | 0.18775 | 0.17522 | 1.0046 | 0.080345 | 0.4377 | 2.4012 | 1.0101 | 0.3367 | 3.511 | 4.266 | 20.09 | 10.06 | 27.867 | 17.837
[18 empty] | 6500 | 14.495 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 6.644 | 6.644 | 4.321 | 6.644 | 6.644 | 0.034273 | 2.4813 | 0.22034 | 0.20564 | 1.179 | 0.093169 | 0.50756 | 2.7844 | 1.1713 | 0.39043 | 4.1206 | 4.9469 | 20.09 | 10.06 | 29.1575 | 19.1275
[18 empty] | 7000 | 15.61 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 7.1551 | 7.1551 | 4.6534 | 7.1551 | 7.1551 | 0.039748 | 2.8778 | 0.25555 | 0.23849 | 1.3673 | 0.10686 | 0.58215 | 3.1936 | 1.3434 | 0.44781 | 4.7789 | 5.6738 | 20.09 | 10.06 | 30.5427 | 20.5127
[18 empty] | 7500 | 16.725 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 7.6662 | 7.6662 | 4.9858 | 7.6662 | 7.6662 | 0.045629 | 3.3035 | 0.29336 | 0.27377 | 1.5696 | 0.12141 | 0.6614 | 3.6284 | 1.5263 | 0.50877 | 5.4859 | 6.4463 | 20.09 | 10.06 | 32.0222 | 21.9922
[18 empty] | 8000 | 17.84 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 8.1773 | 8.1773 | 5.3182 | 8.1773 | 8.1773 | 0.051916 | 3.7587 | 0.33378 | 0.31149 | 1.7859 | 0.1368 | 0.74528 | 4.0885 | 1.7199 | 0.57329 | 6.2418 | 7.2638 | 20.09 | 10.06 | 33.5955 | 23.5655
[18 empty] | 8500 | 18.955 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 8.6883 | 8.6883 | 5.6506 | 8.6883 | 8.6883 | 0.058608 | 4.2432 | 0.3768 | 0.35165 | 2.0161 | 0.15304 | 0.83373 | 4.5738 | 1.924 | 0.64133 | 7.0464 | 8.1259 | 20.09 | 10.06 | 35.2623 | 25.2323
MINOR LOSSES | K | qty |  | MINOR LOSSES | K | qty |  | MINOR LOSSES | K |  |  | MINOR LOSSES | K |  | MINOR LOSSES | K |  | 9000 | 20.07 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 9.1994 | 9.1994 | 5.983 | 9.1994 | 9.1994 | 0.065706 | 4.7571 | 0.42244 | 0.39424 | 2.2603 | 0.17011 | 0.92672 | 5.0839 | 2.1386 | 0.71286 | 7.8998 | 9.0322 | 20.09 | 10.06 | 37.022 | 26.992
Entry Losses | 0.5 | 1 |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  |  | Entry Losses | 0.5 |  | Entry Losses | 0.5 | qty | 9500 | 21.185 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 9.7105 | 9.7105 | 6.3154 | 9.7105 | 9.7105 | 0.073209 | 5.3004 | 0.47068 | 0.43926 | 2.5184 | 0.188 | 1.0242 | 5.6187 | 2.3636 | 0.78786 | 8.8019 | 9.9824 | 20.09 | 10.06 | 38.8743 | 28.8443
Reducer |  |  |  | Reducer |  |  |  | Reducer |  |  |  | Reducer |  | 1 | Reducer |  | 0 | 10000 | 22.3 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 10.2216 | 10.2216 | 6.6477 | 10.2216 | 10.2216 | 0.081118 | 5.873 | 0.52153 | 0.48671 | 2.7905 | 0.20672 | 1.1262 | 6.178 | 2.5988 | 0.86628 | 9.7528 | 10.976 | 20.09 | 10.06 | 40.8188 | 30.7888
Bellmouth | 0.05 | 1 |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  |  | Bellmouth | 0.05 |  | Bellmouth | 0.05 |  | 10600 | 23.638 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 10.8349 | 10.8349 | 7.0466 | 10.8349 | 10.8349 | 0.091145 | 6.5989 | 0.58599 | 0.54687 | 3.1354 | 0.23025 | 1.2543 | 6.8812 | 2.8946 | 0.96488 | 10.9582 | 12.2253 | 20.09 | 10.06 | 43.2736 | 33.2436
Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  |  | Rounded | 0.25 |  | Rounded | 0.25 |  | 10800 | 24.084 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 11.0393 | 11.0393 | 7.1796 | 11.0393 | 11.0393 | 0.094616 | 6.8502 | 0.60831 | 0.5677 | 3.2548 | 0.23835 | 1.2985 | 7.1233 | 2.9965 | 0.99883 | 11.3757 | 12.6555 | 20.09 | 10.06 | 44.1211 | 34.0911
Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  |  | Sharp Edged | 0.5 |  | Sharp Edged | 0.5 |  | 11000 | 24.53 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 11.2437 | 11.2437 | 7.3125 | 11.2437 | 11.2437 | 0.098153 | 7.1063 | 0.63105 | 0.58892 | 3.3765 | 0.24658 | 1.3433 | 7.3693 | 3.1 | 1.0333 | 11.8009 | 13.0925 | 20.09 | 10.06 | 44.9833 | 34.9533
Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  |  | Projecting | 0.8 |  | Projecting | 0.8 |  | 11500 | 25.645 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 11.7548 | 11.7548 | 7.6449 | 11.7548 | 11.7548 | 0.10728 | 7.767 | 0.68972 | 0.64367 | 3.6904 | 0.26771 | 1.4585 | 8.0009 | 3.3657 | 1.1219 | 12.8981 | 14.2146 | 20.09 | 10.06 | 47.2027 | 37.1727
Exit Loss | 1 |  |  | Exit Loss | 1 |  |  | Exit Loss | 1 |  |  | Exit Loss | 1 | 0 | Exit Loss | 1 | 1 | 12000 | 26.76 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 12.2659 | 12.2659 | 7.9773 | 12.2659 | 12.2659 | 0.11681 | 8.4571 | 0.751 | 0.70086 | 4.0183 | 0.28964 | 1.5779 | 8.6563 | 3.6414 | 1.2138 | 14.044 | 15.3791 | 20.09 | 10.06 | 49.5131 | 39.4831
90 deg Ell, std | 0.36 | 0 |  | 90 deg Ell, std | 0.36 | 4 |  | 90 deg Ell, std | 0.36 | 0 |  | 90 deg Ell, std | 0.36 |  | 90 deg Ell, std | 0.36 |  | 12500 | 27.875 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 12.777 | 12.777 | 8.3097 | 12.777 | 12.777 | 0.12675 | 9.1765 | 0.81488 | 0.76048 | 4.3601 | 0.31237 | 1.7017 | 9.3354 | 3.927 | 1.309 | 15.2387 | 16.5855 | 20.09 | 10.06 | 51.9142 | 41.8842
91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  |  | 91 deg Ell, long radius | 0.19 |  | 91 deg Ell, long radius | 0.19 |  | 13000 | 28.99 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 13.288 | 13.288 | 8.6421 | 13.288 | 13.288 | 0.13709 | 9.9253 | 0.88138 | 0.82254 | 4.7159 | 0.33587 | 1.8298 | 10.0379 | 4.2225 | 1.4075 | 16.4822 | 17.8336 | 20.09 | 10.06 | 54.4059 | 44.3759
45 deg Ell, std | 0.19 |  |  | 45 deg Ell, std | 0.19 | 2 |  | 45 deg Ell, std | 0.19 | 4 |  | 45 deg Ell, std | 0.19 |  | 45 deg Ell, std | 0.19 |  | 13500 | 30.105 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 13.7991 | 13.7991 | 8.9745 | 13.7991 | 13.7991 | 0.14784 | 10.7035 | 0.95048 | 0.88703 | 5.0856 | 0.36016 | 1.9621 | 10.7638 | 4.5279 | 1.5093 | 17.7745 | 19.1233 | 20.09 | 10.06 | 56.9877 | 46.9577
45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  |  | 45 deg Ell, long radius | 0.1 |  | 45 deg Ell, long radius | 0.1 |  | 14000 | 31.22 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 14.3102 | 14.3102 | 9.3068 | 14.3102 | 14.3102 | 0.15899 | 11.511 | 1.0222 | 0.95395 | 5.4693 | 0.38523 | 2.0986 | 11.5129 | 4.843 | 1.6143 | 19.1155 | 20.4542 | 20.09 | 10.06 | 59.6596 | 49.6296
Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  |  | Tee, line flow | 0.24 |  | Tee, line flow | 0.24 |  | 14500 | 32.335 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 14.8213 | 14.8213 | 9.6392 | 14.8213 | 14.8213 | 0.17055 | 12.3479 | 1.0965 | 1.0233 | 5.867 | 0.41107 | 2.2394 | 12.2851 | 5.1679 | 1.7226 | 20.5052 | 21.8261 | 20.09 | 10.06 | 62.4213 | 52.3913
Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 |  | Tee, branch flow | 0.72 | 0 | Tee, branch flow | 0.72 | 1 | 15000 | 33.45 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 15.3324 | 15.3324 | 9.9716 | 15.3324 | 15.3324 | 0.18252 | 13.2142 | 1.1734 | 1.0951 | 6.2786 | 0.43767 | 2.3844 | 13.0803 | 5.5023 | 1.8341 | 21.9438 | 23.2388 | 20.09 | 10.06 | 65.2726 | 55.2426
Coupling | 0.04 |  |  | Coupling | 0.04 |  |  | Coupling | 0.04 |  |  | Coupling | 0.04 |  | Coupling | 0.04 |  | 15500 | 34.565 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 15.8434 | 15.8434 | 10.304 | 15.8434 | 15.8434 | 0.19489 | 14.1098 | 1.253 | 1.1693 | 6.7041 | 0.46504 | 2.5335 | 13.8983 | 5.8465 | 1.9488 | 23.4311 | 24.6921 | 20.09 | 10.06 | 68.2132 | 58.1832
Union | 0.04 |  |  | Union | 0.04 |  |  | Union | 0.04 |  |  | Union | 0.04 |  | Union | 0.04 |  | 16000 | 35.68 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 16.3545 | 16.3545 | 10.6364 | 16.3545 | 16.3545 | 0.20766 | 15.0348 | 1.3351 | 1.246 | 7.1436 | 0.49318 | 2.6867 | 14.7391 | 6.2001 | 2.0667 | 24.9672 | 26.1859 | 20.09 | 10.06 | 71.243 | 61.213
Butterfly Valve, Open | 0.3 | 0 |  | Butterfly Valve, Open | 0.3 | 2 |  | Butterfly Valve, Open | 0.3 |  |  | Butterfly Valve, Open | 0.3 | 1 | Butterfly Valve, Open | 0.3 | 0 | 16500 | 36.795 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 16.8656 | 16.8656 | 10.9688 | 16.8656 | 16.8656 | 0.22084 | 15.9892 | 1.4199 | 1.3251 | 7.5971 | 0.52207 | 2.8441 | 15.6025 | 6.5633 | 2.1878 | 26.552 | 27.7198 | 20.09 | 10.06 | 74.3618 | 64.3318
Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  |  | Gate Valve, open | 0.1 |  | Gate Valve, open | 0.1 |  | 17000 | 37.91 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 17.3767 | 17.3767 | 11.3012 | 17.3767 | 17.3767 | 0.23443 | 16.9729 | 1.5072 | 1.4066 | 8.0645 | 0.55171 | 3.0056 | 16.4885 | 6.936 | 2.312 | 28.1856 | 29.2938 | 20.09 | 10.06 | 77.5694 | 67.5394
Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  |  | Gate Valve, 3/4 open | 0.9 |  | Gate Valve, 3/4 open | 0.9 |  | 17500 | 39.025 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 17.8877 | 17.8877 | 11.6335 | 17.8877 | 17.8877 | 0.24842 | 17.986 | 1.5972 | 1.4905 | 8.5458 | 0.5821 | 3.1712 | 17.3968 | 7.3181 | 2.4394 | 29.8679 | 30.9076 | 20.09 | 10.06 | 80.8655 | 70.8355
Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  |  | Gate Valve, 1/2 open | 4.5 |  | Gate Valve, 1/2 open | 4.5 |  | 18000 | 40.14 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 18.3988 | 18.3988 | 11.9659 | 18.3988 | 18.3988 | 0.26282 | 19.0284 | 1.6897 | 1.5769 | 9.0411 | 0.61325 | 3.3408 | 18.3275 | 7.7096 | 2.5699 | 31.5991 | 32.5611 | 20.09 | 10.06 | 84.2502 | 74.2202
Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  |  | Gate Valve, 1/4 open | 24 |  | Gate Valve, 1/4 open | 24 |  | 18500 | 41.255 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 18.9099 | 18.9099 | 12.2983 | 18.9099 | 18.9099 | 0.27763 | 20.1002 | 1.7849 | 1.6658 | 9.5504 | 0.64513 | 3.5145 | 19.2804 | 8.1105 | 2.7035 | 33.3789 | 34.2541 | 20.09 | 10.06 | 87.723 | 77.693
Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  |  | Cross, line flow | 0.5 |  | Cross, line flow | 0.5 |  | 19000 | 42.37 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 19.421 | 19.421 | 12.6307 | 19.421 | 19.421 | 0.29284 | 21.2014 | 1.8827 | 1.757 | 10.0736 | 0.67776 | 3.6923 | 20.2555 | 8.5207 | 2.8402 | 35.2076 | 35.9865 | 20.09 | 10.06 | 91.284 | 81.254
Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  |  | Cross, branch flow | 0.75 |  | Cross, branch flow | 0.75 |  | 19500 | 43.485 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 19.9321 | 19.9321 | 12.9631 | 19.9321 | 19.9321 | 0.30845 | 22.332 | 1.9831 | 1.8507 | 10.6108 | 0.71112 | 3.8741 | 21.2527 | 8.9401 | 2.98 | 37.085 | 37.758 | 20.09 | 10.06 | 94.933 | 84.903
Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  |  | Wye | 0.5 |  | Wye | 0.5 |  | 20000 | 44.6 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 20.4431 | 20.4431 | 13.2955 | 20.4431 | 20.4431 | 0.32447 | 23.4919 | 2.0861 | 1.9468 | 11.1619 | 0.74522 | 4.0598 | 22.2718 | 9.3688 | 3.1229 | 39.0112 | 39.5686 | 20.09 | 10.06 | 98.6698 | 88.6398
Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  |  | Ball Check Valve | 0.66 |  | Ball Check Valve | 0.66 |  | 20500 | 45.715 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 20.9542 | 20.9542 | 13.6279 | 20.9542 | 20.9542 | 0.3409 | 24.6811 | 2.1917 | 2.0454 | 11.727 | 0.78005 | 4.2496 | 23.3128 | 9.8067 | 3.2689 | 40.9861 | 41.418 | 20.09 | 10.06 | 102.4942 | 92.4642
Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  |  | Rubber swingcheck valve | 1.2 |  | Rubber swingcheck valve | 1.2 |  | 21000 | 46.83 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 21.4653 | 21.4653 | 13.9603 | 21.4653 | 21.4653 | 0.35773 | 25.8998 | 2.2999 | 2.1464 | 12.306 | 0.81562 | 4.4433 | 24.3756 | 10.2538 | 3.4179 | 43.0098 | 43.3063 | 20.09 | 10.06 | 106.4061 | 96.3761
Metal swing check valve | 1.2 | 0 |  | Metal swing check valve | 1.2 | 1 |  | Metal swing check valve | 1.2 |  |  | Metal swing check valve | 1.2 |  | Metal swing check valve | 1.2 |  | 21500 | 47.945 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 21.9764 | 21.9764 | 14.2926 | 21.9764 | 21.9764 | 0.37497 | 27.1478 | 2.4108 | 2.2498 | 12.899 | 0.85191 | 4.641 | 25.4601 | 10.71 | 3.57 | 45.0823 | 45.2331 | 20.09 | 10.06 | 110.4054 | 100.3754
Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  |  | Gate Valve | 0.1 |  | Gate Valve | 0.1 |  | 22000 | 49.06 | 2.1817 | 2.1817 | 3.3545 | 2.1817 | 2.1817 | 22.4874 | 22.4874 | 14.625 | 22.4874 | 22.4874 | 0.39261 | 28.4252 | 2.5242 | 2.3557 | 13.5059 | 0.88892 | 4.8427 | 26.5663 | 11.1753 | 3.7251 | 47.2035 | 47.1984 | 20.09 | 10.06 | 114.4919 | 104.4619
Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  |  | Ball Valve | 0.04 |  | Ball Valve | 0.04
TOTAL K IN APP | 0.05 |  |  | TOTAL K IN APP | 3.62 |  |  | TOTAL K IN APP | 0.76 |  |  | TOTAL K IN APP | 0.3 |  | TOTAL K IN APP | 1.72
Note on B27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on F27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on J27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on N27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on R27: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4

## Recovery Wet Well Calcs
Min. Depth (ft) | 6.4
Pump Start Depth | 7
Max. Depth (ft) | 10 | [9 empty] | Flow | Flow | Duration | Volume
Overflow Depth | 10.17 |  |  | Determine Wet Well Invert & Float Elevations | [5 empty] | BWW Cycle | gpm/sf | gpm | MIN | Gal
[10 empty] | Surface Wash Flow | 0 |  | 0 | 0
Wet Well Compartment 1 |  |  |  | Top Elev= | 5191.32 |  |  |  |  | Wash Ramp Up | 3 | 1800 | 1 | 1800 | 240.6417
Length (ft) | 25 |  |  | Gnd Elev= | 5191 |  |  |  |  | Wash Flow | 9 | 5400 | 1 | 5400 | 721.9251
Width (ft) | 19.4167 | [8 empty] | Hi Wash Flow | 18 | 10800 | 10 | 108000 | 14438.5027
Min Volume (ft^3) | 3106.6667 | [8 empty] | Wash Ramp Down | 9 | 5400 | 1.5 | 8100 | 1082.8877
Pump Start Volume (ft^3) | 3397.9167
Max Volume (ft^3) | 4854.1667 | [6 empty] | Overflow = | 10.18 | Wash Ramp Down | 3 | 1800 | 1.5 | 2700 | 360.9626
Overflow Volume (ft^3) | 4936.6875 | [6 empty] | Alarm = | 10 | Total |  |  | 15 | 126000
Min Volume (gal) | 23237.8667 | [6 empty] | Lag On = | 8.4
Pump Start Volume (gal) | 25416.4167 | [6 empty] | Lead On = | 7.4
Max. Volume (gal) | 36309.1667 | [6 empty] | Pumps Off = | 6.4
Overflow Volume (gal) | 36926.4225 |  |  | Invert In= | 5174.83 |  |  |  |  | Sludge Blow Down
Wet Well Compartment 2 | [9 empty] | Flow Rate From Sludge Collector |  | 150 | gpm
Length (ft) | 25 |  |  | Bottom Invert Elev* = | 5169.82 |  |  | Bottom | 0 | Collector Speed |  | 0.5 | ft/mn
Width (ft) | 15.4167 | [8 empty] | Length of Travel |  | 80 | ft
Depth (ft) | 11.19 | [8 empty] | Time per pass |  | 160 | mn
Min Volume (ft^3) | 2466.6667 |  |  | Cross Sectional Area = | 870.8333 | ft2 |  |  |  | Total Flow |  | 24000 | gallons
Pump Start Volume (ft^3) | 2697.9167 |  |  | Time | Total Volume In | Total Volume Out | Level
Max Volume (ft^3) | 3854.1667 |  |  | 1 | 240.6417 | 0 | 6.6763
Overflow Volume (ft^3) | 3919.6875 |  |  | 1.8729 | 630.1916 | 0 | 7.4 | pump start
Min Volume (gal) | 18450.6667 |  |  | 2 | 91.7335 | 163.4093 | 7.3177 | 1 pump at 9675 gpm or 1296 ft3/min
Pump Start Volume | 20180.4167 |  |  | 3 | 1443.8503 | 1286 | 7.499 | 1 pump at 9675 gpm or 1296 ft3/min
Max. Volume (gal) | 28829.1667 |  |  | 4 | 1443.8503 | 1286 | 7.6802 | 1 pump at 9675 gpm or 1296 ft3/min
Max. Volume (gal) | 29319.2625 |  |  | 5 | 1443.8503 | 1286 | 7.8615 | 1 pump at 9675 gpm or 1296 ft3/min
|  |  |  | 6 | 1443.8503 | 1286 | 8.0427 | 1 pump at 9675 gpm or 1296 ft3/min
Total Volume (gal) |  |  |  | 7 | 1443.8503 | 1286 | 8.224 | 1 pump at 9675 gpm or 1296 ft3/min
Min. | 41688.5333 |  |  | 8 | 1443.8503 | 1286 | 8.4053 | 1 pump at 9675 gpm or 1296 ft3/min
Pump Start Volume | 45596.8333 |  |  | 9 | 1443.8503 | 1286 | 8.5865 | 1 pump at 9675 gpm or 1296 ft3/min
Max. | 65138.3333 |  |  | 10 | 1443.8503 | 1286 | 8.7678 | 1 pump at 9675 gpm or 1296 ft3/min
Overflow Volume | 66245.685 |  |  | 11 | 1443.8503 | 1286 | 8.9491 | 1 pump at 9675 gpm or 1296 ft3/min
|  |  |  | 12 | 1443.8503 | 1286 | 9.1303 | 1 pump at 9675 gpm or 1296 ft3/min
Usable Volume (gal) | 19541.5 |  |  | 13 | 721.9251 | 1286 | 8.4826 | 1 pump at 9675 gpm or 1296 ft3/min
|  |  |  | 13.5 | 360.9626 | 643 | 8.1587 | 1 pump at 9675 gpm or 1296 ft3/min
|  |  |  | 14 | 120.3209 | 643 | 7.5585 | 1 pump at 9675 gpm or 1296 ft3/min
Qin | 10800 | gpm | (assume high wash for one filter only, no sludge blow down) | 15 | 240.6417 | 1270 | 6.3765 | 1 pump at 9675 gpm or 1296 ft3/min
Qout | 10625 | gpm | (one pump out of service) | 15.15 | 0 | 190.5 | 6.1577
Qdelta | 175 | gpm
Volume | 1750 | gal
Time to overflow | 119.9934 | minutes
Times to fill wet well
Time to fill wet well | 111.6657 | min
Backwash duration | 10 | minimum
Design OK

## HI Standard
Intake Geometry Calcs
FD= | Froude Number |  | FD= | Froude Number
FD= | V/(gD).5 |  | FD= | V/(gD).5
D= | Outside Diameter of Pump Bell |  | D= | Outside Diameter of Pump Bell
D= | 2.5833 | ft | D= | 2.5833
Q= | 13.1 | MGD | Q= | 2.6
Q= | 10800 | gpm | Q= | 1805.44
Q= | 24.0642 | cfs | Q= | 4.0228
V= | 4.5913 |  | V= | 0.76752
FD= | 0.5034 |  | FD= | 0.084154 | ft
S= | Min Submergence |  | S= | Min Submergence
S= | D(1+2.3FD) |  | S= | D(1+2.3FD)
S= | 5.5743 | ft | S= | 3.0833 | ft
S= | 66.8918 | inches
Pump Height Above Floor = | .5D |  | Pump Height Above Floor = | .5D
Pump Height above Floor = | 1.2916 | ft | Pump Height above Floor = | 1.2916 | ft
Min Water Level | 6.866 |  | Min Water Level | 4.375
Wet Well Floor El: | 5169.82
Min Water Level | 5176.686
Pump Offset off Backwall = | .75D |  | Pump Offset off Backwall = | .75D
Pump Offset off of Backwall = | 1.9375 | ft | Pump Offset off of Backwall = | 1.9375 | ft
Pump Bay Width = | 2D |  | Pump Bay Width = | 2D
Pump Bay Width = | 5.1666 |  | Pump Bay Width = | 5.1666
Pump Bay Length = | 5D |  | Pump Bay Length = | 5D
Pump Bay Length = | 12.9165 |  | Pump Bay Length = | 12.9165

## BPS Drawings
8.4
6.4
7.4

## EQ Basin Cad Image
Low Water Level is 5186.75 - Translated to the new Datum (+3.32 ft) = 5190.7

## BWR Sys Curve - Replace 20" Sec
SYSTEM CURVE
| Min. Wet Well WSE | 5172.32 | Current pump 1 on depth |  | Existing Set Points in Wetwell
| Max. Wet Well EL | 5179.9867 | OVF |  | Low | 5 | ft |  | Describe What Seg 1 and 2 include, need separate segments for VT Pump Column and Discharge Heard
| Exit EL | 5196 | Best guess, to be confirmed with 2004 B&C Drawings |  | High Alarm | 10 | ft |  | We cannot stamp an 11 fps velocity.
|  |  | Have we Confirmed? See New Drawing Worksheed |  | High High | 10.2 | ft
STATIC HEAD |  |  | Need to Add Max and Min EQ Level to spreadsheet |  |  |  |  | Flow |  | Seg 1 Area | Seg 2 Area | Seg 1 Velocity | Seg 2 Velocity | Seg 1 h_minor | Seg 2 h_minor | Seg 1 h_friction | Seg 2 h_friction | Seg 2 h total | h_delta_max | h_delta_min | TDH Max | TDH Min
Max. Total Static Head |  | 23.68 | [5 empty] | gpm | cfs | sf | sf | fps | fps | ft | ft | ft | ft | ft | ft | ft | ft | ft
Min Total Static Head |  | 16.0133 | [5 empty] | 0 | 0 | 3.1416 | 3.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.68 | 16.0133 | 23.68 | 16.0133
[8 empty] | 500 | 1.115 | 3.1416 | 3.1416 | 0.35492 | 0.35492 | 0.0049877 | 0.0047921 | 0.038412 | 0.0041905 | 0.0089826 | 23.68 | 16.0133 | 23.7414 | 16.0657
FRICTION LOSS | [7 empty] | 1000 | 2.23 | 3.1416 | 3.1416 | #NAME? | 0.70983 | #NAME? | 0.019169 | 0.13848 | 0.015107 | 0.034275 | 23.68 | 16.0133 | #NAME? | #NAME?
Hazen Williams Coefficients |  | C_water | C_wastewater |  |  |  |  | 1500 | 3.345 | 3.1416 | 3.1416 | 1.0647 | 1.0647 | 0.04489 | 0.043129 | 0.29319 | 0.031984 | 0.075114 | 23.68 | 16.0133 | 24.1683 | 16.4265
DI |  | 80-120 | 80-110 |  |  |  |  | 2000 | 4.46 | 3.1416 | 3.1416 | 1.4197 | 1.4197 | 0.079804 | 0.076674 | 0.49921 | 0.054459 | 0.13113 | 23.68 | 16.0133 | 24.5213 | 16.7235
Steel |  | 110-130 | 110-130 |  |  |  |  | 2500 | 5.575 | 3.1416 | 3.1416 | 1.7746 | 1.7746 | 0.12469 | 0.1198 | 0.75434 | 0.082292 | 0.2021 | 23.68 | 16.0133 | 24.9632 | 17.0945
PVC |  | 135-150 | 130-145 |  |  |  |  | 3000 | 6.69 | 3.1416 | 3.1416 | 2.1295 | 2.1295 | 0.17956 | 0.17252 | 1.0569 | 0.1153 | 0.28782 | 23.68 | 16.0133 | 25.4921 | 17.5377
[8 empty] | 3500 | 7.805 | 3.1416 | 3.1416 | 2.4844 | 2.4844 | 0.2444 | 0.23482 | 1.4057 | 0.15335 | 0.38817 | 23.68 | 16.0133 | 26.1065 | 18.0516
Segment 1 (Existing 24" BWS Pipe) |  |  |  | Segment 2 (New 20" BWS Pipe) |  |  |  | 4000 | 8.92 | 3.1416 | 3.1416 | 2.8393 | 2.8393 | 0.31922 | 0.3067 | 1.7997 | 0.19633 | 0.50302 | 23.68 | 16.0133 | 26.8049 | 18.6352
hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | hf = (L)(D^-4.87)(10.5)(Q/C)^1.85 |  |  |  | 4500 | 10.035 | 3.1416 | 3.1416 | 3.1942 | 3.1942 | 0.40401 | 0.38816 | 2.2378 | 0.24412 | 0.63229 | 23.68 | 16.0133 | 27.5864 | 19.2874
L = Length of pipe (ft) |  | 1375 | ft | L = Length of pipe (ft) |  | 150 | ft | 5000 | 11.15 | 3.1416 | 3.1416 | 3.5492 | 3.5492 | 0.49877 | 0.47921 | 2.7194 | 0.29666 | 0.77588 | 23.68 | 16.0133 | 28.4499 | 20.0074
D = Inner Diameter of pipe (in) |  | 24 | in | D = Inner Diameter of pipe (in) |  | 24 | in | 5500 | 12.265 | 3.1416 | 3.1416 | 3.9041 | 3.9041 | 0.60352 | 0.57985 | 3.2438 | 0.35386 | 0.93371 | 23.68 | 16.0133 | 29.3947 | 20.7943
C = HW coefficient (table above) |  | 120 |  | C = HW coefficient (table above) |  | 120 |  | 6000 | 13.38 | 3.1416 | 3.1416 | 4.259 | 4.259 | 0.71824 | 0.69007 | 3.8103 | 0.41567 | 1.1057 | 23.68 | 16.0133 | 30.42 | 21.6476
|  | Very Conservative, Consider 120 for old DIP used for Water |  |  |  | 140 for New Pipe per Cameron Hydraulic Data |  | 6500 | 14.495 | 3.1416 | 3.1416 | 4.6139 | 4.6139 | 0.84293 | 0.80987 | 4.4184 | 0.48201 | 1.2919 | 23.68 | 16.0133 | 31.5251 | 22.5666
[8 empty] | 7000 | 15.61 | 3.1416 | 3.1416 | 4.9688 | 4.9688 | 0.9776 | 0.93926 | 5.0677 | 0.55284 | 1.4921 | 23.68 | 16.0133 | 32.7095 | 23.5507
[8 empty] | 7500 | 16.725 | 3.1416 | 3.1416 | 5.3237 | 5.3237 | 1.1222 | 1.0782 | 5.7576 | 0.6281 | 1.7063 | 23.68 | 16.0133 | 33.9725 | 24.5995
[8 empty] | 8000 | 17.84 | 3.1416 | 3.1416 | 5.6786 | 5.6786 | 1.2769 | 1.2268 | 6.4878 | 0.70776 | 1.9345 | 23.68 | 16.0133 | 35.3137 | 25.7125
[8 empty] | 8500 | 18.955 | 3.1416 | 3.1416 | 6.0336 | 6.0336 | 1.4415 | 1.3849 | 7.2578 | 0.79176 | 2.1767 | 23.68 | 16.0133 | 36.7326 | 26.8892
MINOR LOSSES |  | K |  | MINOR LOSSES |  | K |  | 9000 | 20.07 | 3.1416 | 3.1416 | 6.3885 | 6.3885 | 1.616 | 1.5527 | 8.0673 | 0.88007 | 2.4327 | 23.68 | 16.0133 | 38.2287 | 28.1294
Entry Losses |  |  | qty | Entry Losses |  |  | qty | 9500 | 21.185 | 3.1416 | 3.1416 | 6.7434 | 6.7434 | 1.8006 | 1.73 | 8.9159 | 0.97265 | 2.7026 | 23.68 | 16.0133 | 39.8017 | 29.4325
Reducer |  |  |  | Reducer |  | 0.15 | 1 | 10000 | 22.3 | 3.1416 | 3.1416 | 7.0983 | 7.0983 | 1.9951 | 1.9169 | 9.8034 | 1.0695 | 2.9863 | 23.68 | 16.0133 | 41.4512 | 30.7982
Bellmouth |  | 0.005 |  | Bellmouth |  | 0.005 |  | 10500 | 23.415 | 3.1416 | 3.1416 | 7.4532 | 7.4532 | 2.1996 | 2.1133 | 10.7295 | 1.1705 | 3.2838 | 23.68 | 16.0133 | 43.1767 | 32.2262
Rounded |  | 0.25 |  | Rounded |  | 0.25 |  | 10800 | 24.084 | 3.1416 | 3.1416 | 7.6662 | 7.6662 | 2.3271 | 2.2358 | 11.3035 | 1.2331 | 3.4689 | 23.68 | 16.0133 | 44.2484 | 33.1128
Sharp Edged |  | 0.5 |  | Sharp Edged |  | 0.5 |  | 11000 | 24.53 | 3.1416 | 3.1416 | 7.8081 | 7.8081 | 2.4141 | 2.3194 | 11.6938 | 1.2757 | 3.5951 | 23.68 | 16.0133 | 44.978 | 33.7163
Projecting |  | 0.8 |  | Projecting |  | 0.8 |  | 11500 | 25.645 | 3.1416 | 3.1416 | 8.1631 | 8.1631 | 2.6385 | 2.535 | 12.6961 | 1.385 | 3.9201 | 23.68 | 16.0133 | 46.8547 | 35.268
Exit Loss |  | 1 |  | Exit Loss |  | 1 | 1 | 12000 | 26.76 | 3.1416 | 3.1416 | 8.518 | 8.518 | 2.8729 | 2.7603 | 13.7361 | 1.4985 | 4.2588 | 23.68 | 16.0133 | 48.8066 | 36.8811
90 deg Ell, std |  | 0.75 | 2 | 90 deg Ell, std |  | 0.75 |  | 12500 | 27.875 | 3.1416 | 3.1416 | 8.8729 | 8.8729 | 3.1173 | 2.9951 | 14.8136 | 1.616 | 4.6111 | 23.68 | 16.0133 | 50.8332 | 38.5554
91 deg Ell, long radius |  | 0.45 |  | 91 deg Ell, long radius |  | 0.45 |  | 13000 | 28.99 | 3.1416 | 3.1416 | 9.2278 | 9.2278 | 3.3717 | 3.2395 | 15.9284 | 1.7376 | 4.9771 | 23.68 | 16.0133 | 52.9344 | 40.2906
45 deg Ell, std |  | 0.35 | 3 | 45 deg Ell, std |  | 0.35 |  | 13500 | 30.105 | 3.1416 | 3.1416 | 9.5827 | 9.5827 | 3.6361 | 3.4935 | 17.0803 | 1.8633 | 5.3568 | 23.68 | 16.0133 | 55.1099 | 42.0865
45 deg Ell, long radius |  | 0.2 |  | 45 deg Ell, long radius |  | 0.2 |  | 14000 | 31.22 | 3.1416 | 3.1416 | 9.9376 | 9.9376 | 3.9104 | 3.757 | 18.269 | 1.993 | 5.75 | 23.68 | 16.0133 | 57.3594 | 43.9428
Tee, line flow |  | 0.4 |  | Tee, line flow |  | 0.4 |  | 14500 | 32.335 | 3.1416 | 3.1416 | 10.2926 | 10.2926 | 4.1947 | 4.0302 | 19.4943 | 2.1267 | 6.1569 | 23.68 | 16.0133 | 59.6827 | 45.8592
Tee, branch flow |  | 1 | 0 | Tee, branch flow |  | 1 | 1 | 15000 | 33.45 | 3.1416 | 3.1416 | 10.6475 | 10.6475 | 4.489 | 4.3129 | 20.7561 | 2.2643 | 6.5772 | 23.68 | 16.0133 | 62.0796 | 47.8357
Coupling |  | 0.04 |  | Coupling |  | 0.04 |  | 15500 | 34.565 | 3.1416 | 3.1416 | 11.0024 | 11.0024 | 4.7932 | 4.6053 | 22.0542 | 2.4059 | 7.0112 | 23.68 | 16.0133 | 64.5498 | 49.8719
Union |  | 0.04 |  | Union |  | 0.04 |  | 16000 | 35.68 | 3.1416 | 3.1416 | 11.3573 | 11.3573 | 5.1075 | 4.9072 | 23.3884 | 2.5515 | 7.4586 | 23.68 | 16.0133 | 67.0931 | 51.9678
Butterfly Valve, Open |  | 0.3 |  | Butterfly Valve, Open |  | 0.3 | 1 | 16500 | 36.795 | 3.1416 | 3.1416 | 11.7122 | 11.7122 | 5.4317 | 5.2186 | 24.7584 | 2.7009 | 7.9196 | 23.68 | 16.0133 | 69.7092 | 54.123
Gate Valve, open |  | 0.17 |  | Gate Valve, open |  | 0.17 |  | 17000 | 37.91 | 3.1416 | 3.1416 | 12.0671 | 12.0671 | 5.7658 | 5.5397 | 26.1643 | 2.8543 | 8.394 | 23.68 | 16.0133 | 72.3981 | 56.3374
Gate Valve, 3/4 open |  | 0.9 |  | Gate Valve, 3/4 open |  | 0.9 |  | 17500 | 39.025 | 3.1416 | 3.1416 | 12.422 | 12.422 | 6.11 | 5.8704 | 27.6057 | 3.0115 | 8.8819 | 23.68 | 16.0133 | 75.1595 | 58.6109
Gate Valve, 1/2 open |  | 4.5 |  | Gate Valve, 1/2 open |  | 4.5 |  | 18000 | 40.14 | 3.1416 | 3.1416 | 12.777 | 12.777 | 6.4641 | 6.2106 | 29.0825 | 3.1726 | 9.3833 | 23.68 | 16.0133 | 77.9932 | 60.9432
Gate Valve, 1/4 open |  | 24 |  | Gate Valve, 1/4 open |  | 24 |  | 18500 | 41.255 | 3.1416 | 3.1416 | 13.1319 | 13.1319 | 6.8282 | 6.5605 | 30.5947 | 3.3376 | 9.898 | 23.68 | 16.0133 | 80.899 | 63.3343
Cross, line flow |  | 0.5 |  | Cross, line flow |  | 0.5 |  | 19000 | 42.37 | 3.1416 | 3.1416 | 13.4868 | 13.4868 | 7.2023 | 6.9199 | 32.1419 | 3.5064 | 10.4263 | 23.68 | 16.0133 | 83.8768 | 65.7838
Cross, branch flow |  | 0.75 |  | Cross, branch flow |  | 0.75 |  | 19500 | 43.485 | 3.1416 | 3.1416 | 13.8417 | 13.8417 | 7.5864 | 7.2889 | 33.7242 | 3.679 | 10.9679 | 23.68 | 16.0133 | 86.9263 | 68.2918
Wye |  | 0.5 |  | Wye |  | 0.5 |  | 20000 | 44.6 | 3.1416 | 3.1416 | 14.1966 | 14.1966 | 7.9804 | 7.6674 | 35.3414 | 3.8554 | 11.5229 | 23.68 | 16.0133 | 90.0475 | 70.858
Ball Check Valve |  | 1.7 |  | Ball Check Valve |  | 1.7 |  | 20500 | 45.715 | 3.1416 | 3.1416 | 14.5515 | 14.5515 | 8.3844 | 8.0556 | 36.9933 | 4.0356 | 12.0912 | 23.68 | 16.0133 | 93.2401 | 73.4822
Rubber swingcheck valve |  | 1.1 |  | Rubber swingcheck valve |  | 1.1 |  | 21000 | 46.83 | 3.1416 | 3.1416 | 14.9065 | 14.9065 | 8.7984 | 8.4533 | 38.6797 | 4.2196 | 12.673 | 23.68 | 16.0133 | 96.504 | 76.1644
Metal swing check valve |  | 1.5 |  | Metal swing check valve |  | 1.5 |  | 21500 | 47.945 | 3.1416 | 3.1416 | 15.2614 | 15.2614 | 9.2223 | 8.8607 | 40.4007 | 4.4074 | 13.268 | 23.68 | 16.0133 | 99.8391 | 78.9044
Gate Valve |  | 0.3 |  | Gate Valve |  | 0.3 |  | 22000 | 49.06 | 3.1416 | 3.1416 | 15.6163 | 15.6163 | 9.6563 | 9.2776 | 42.156 | 4.5988 | 13.8764 | 23.68 | 16.0133 | 103.2452 | 81.7021
Ball Valve |  | 0.04 |  | Ball Valve |  | 0.04
TOTAL K IN APP |  | 2.55 |  | TOTAL K IN APP |  | 2.45
Note on C26: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4
Note on H26: Jarod Limke: Perry, 1997 chap 6 pp. 18, table 6-4